## 2023 Updates
CRG Updates 2023
REVISION | EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
UPDATED JAN-2023 | Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age | N/A | http://ehs.psu.edu/ppe/overview | All except office
NEW ADDITION JAN-2023 | Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
NEW ADDITION JAN-2023 | Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
NEW ADDITION JAN-2023 | Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
UPDATED JAN-2023 | Environmental Emergency Plan / Storage Tanks | PADEP Regulated Storage Tank inspection by PADEP | Varies | Certain PA DEP regulated storage tanks must have an inspection a PA DEP certified inspection as directed on storage tank registration | Life of equipment |  | Maintenance
UPDATED JAN-2023 | Environmental Emergency Plans | Spill kits | Varies | Maintain and re-stock spill kits in elevator mechanical rooms, laboratories, machine shops, kitchens, storage tank locations, and other areas that require spill response kits. | N/A | http://ehs.psu.edu/environmental-emergency-plans/overview | Any | replacement costs
UPDATED JAN-2023 | Environmental Emergency Plans | Spill response training for hazardous materials, oils, and/or storage tanks | Annual | Provide EHERP training to affected employees annually | End of calendar year in which course ends or separation of employment + 30 years |  | Maintenance, Labs, Housing & Food Service
UPDATED JAN-2023 | Environmental Emergency Plans | Tier II reporting (SARA) | Due March 1st | Report of any chemical (including road salt and other ice melting products) that exceeds the Threshold Planning Quantity, generally 10,000 pounds or more | Superseded/ outdated + 1 year | https://www.lipatts.pa.gov/Account/Login.aspx | Maintenance
UPDATED JAN-2023 | Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Annual - June | Visual inspection of aboveground storage tanks; this is more comprehensive than the monthly inspection. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/annual_aboveground_storage_tank_inspection_checklist_ehs-064_rev_5-21.docx | Maintenance
UPDATED JAN-2023 | Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Monthly | Visual inspection of aboveground storage tanks; there are two forms, one for fuel/oil storage tanks and one for chemical storage tanks. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_aboveground_storage_tank_inspection_checklist_ehs-062_rev_5-21.docx | Maintenance
https://ehs.psu.edu/sites/ehs/files/monthly_chemical_aboveground_storage_tank_inspection_checklist_ehs-063_rev_5-21.docx
UPDATED JAN-2023 | Environmental Emergency Plans / Storage Tanks | Underground tank facility inspection | Monthly | Underground tank facility general inspection | End of calendar year + 3 years |  | Maintenance | Varies by tank size
NEW ADDITION JAN-2023 | Pesticides | Worker Protection Standard Training | Annual | All employees who are not certified applicators and who work in areas where pesticides are used for agricultural applications, including greenhouses, must take annual training. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs/farms/research using pesticides
UPDATED JAN-2023 | Refrigerant | Leak Rate Calculations | Varies | For all appliances containing 50 pounds or more of refrigerant in a circuit, leak rates must be calculated each time refrigerant is added. There is a spreadsheet which performs these calculations. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
NEW ADDITION JAN-2023 | Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
UPDATED JAN-2023 | Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
UPDATED JAN-2023 | Fire Prevention/Protection | Building Fire Protection Pumps | Annual | Annual pump inspection and flow test (per NFPA 25) - full flow/performance test and inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
UPDATED JAN-2023 | Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
UPDATED JAN-2023 | Fire Prevention/Protection | Dry sprinkler/fire suppression systems dry pipe trip test | Annual | Conduct partial trip test annually | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
UPDATED JAN-2023 | Fire Prevention/Protection | Automatic Sprinkler System main drain flow test | Annual | Test main drain flow annually (per NFPA 25) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
UPDATED JAN-2023 | Fire Prevention/Protection | Fire Hydrant testing | Annual | Flushing/testing of fire hydrant by water authority or campus staff | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
UPDATED JAN-2023 | Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
UPDATED JAN-2023 | Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
UPDATED JAN-2023 | Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
UPDATED JAN-2023 | Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
UPDATED JAN-2023 | Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
UPDATED JAN-2023 | Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
UPDATED JAN-2023 | Radiation | Radioactive material safety training | Annual | All users of radioactive materials must complete Initial training prior to using material, and refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS-Radionuclide Safety Education | Labs using Radioactive Materials
UPDATED JAN-2023 | Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance

## Read Me Instructions
Read Me: Instructions
Background: This EHS Compliance Requirements Guide (CRG) is a tool that can be used to help track the requirements for all of EHS programs that apply to a particular work area. We have created it so that it can be customized to cover only the programs that apply to your work unit, and we hope it will help you to be better prepared for future audits and potential regulatory compliance inspections. It can be used in conjunction with the Laboratory and Research Safety Plan's Unit Specific Plan or the Self-Review Process in the Integrated Safety Plan for the programs that apply to your work unit. It can also be used by any unit that is looking for an easy way to organize safety responsibilities. Users will probably need to have some familiarity with Excel to take advantage of many of the features, however it can also be printed out and used with handwritten notes. It is set up to be printed on 11" x 17" paper in landscape mode.
How the CRG is organized: The CRG is organized as a typical spreadsheet with rows and columns. The column headings include the following: · EHS program overseeing the requirement · Program requirement · Frequency with which the requirement must be met · Details on how to comply · Recordkeeping requirements · Link to the relevant webpage when applicable. · Departments typically affected · Associated costs · Details on how to comply · Work unit person responsible and backup person
Program Example: The first program listed in the next tab (Master CRG) of this spreadsheet is the AED program. The program requires an inspection of the AED on a monthly basis. The inspection forms from these inspections are retained in your records for three years beyond the end of the calendar year. (This means that you will keep all of your year 2020 inspection forms until January 2024, and all of your 2021 forms until January 2025, etc..) The link takes you to the AED inspection document on our website. There is a column for you to assign this task to someone and to have a backup person for when the primary AED inspector is out.
Program Information: As you look at the "Master CRG" sheet, you can see all of the programs that we have. As you will notice, many of the programs have several requirements, such as trainings and inspections. · Not all of the programs listed apply to any one work unit, so we have created some example sheets with the programs that would typically apply to specific work areas such as Maintenance, Housing & Food Services, IT, and different academic groups such as Chemistry labs or Art studios. There is also a "Classroom & Office" tab that lists the safety requirements that apply to folks whose work is administrative or teaching and does not involve labs, shops, machinery, etc. · The tabs are in alphabetical order by example group, and are color-coded (blue for academics, white for everyone else).
Customizing the worksheet for your group: In the sheet that best applies to your work group, you can delete all of the rows that do not apply to your work area to customize the worksheet The sheets are set up to apply to a wide variety of areas. For example, an Engineering department at a small campus may not have Cranes/Hoists, while one at a larger campus might have several. We have kept some seemingly unrelated programs on academic pages because research is highly diverse. Eyewashes in a laboratory and fire extinguishers in the hallway may be inspected by Campus Maintenance, or your department Safety Officer, or someone else. Each campus is different, so we've given you the full list so you don't miss anything. You can delete any lines that you know don't apply to your work unit. To delete lines you don't want, hover the mouse over the gray box that has the line number in it. Right-clicking the box will produce a drop-down menu, and from that menu you can choose "delete". Now that you have the CRG set up for your work group, what should you use it for? You really can use it anyway you want! See the ideas listed below:
A. Search for or sort the "Program Requirement" column to find all of the items that involve a required training. ·You can then schedule or assign the training to make sure everyone gets it. B: Search for or sort to group the "inspections". Some need to be done every week, while others are monthly, semi-annual, or annual. C: You can assign these tasks into your work order system (Maximo, SchoolDude, etc.) or your electronic calendar, to ensure that they get completed at the proper frequency.
Notes: · Whether or not you use a work order system, you can also fill in the "Work Unit Person Responsible and Backup" and post it in the work area so that your employees know who should be completing a given compliance task when the employee who usually does it is out. · This may help prevent you from missing important regulatory requirements such as the weekly eyewash test or the weekly inspection of a chemical waste satellite accumulation area when the person who usually does it is out. You can also sort by "Work Unit Person Responsible and Backup" and print those out for individual employees.
If you have any difficulty in using the EHS Compliance Requirements Guide, or ideas of how to make this more useful or easier to use, please feel free to contact us at EHS at: https://ehs.psu.edu/contact-us. We welcome your feedback.
* To use the sort function in Excel, follow these steps: 1. Click on the gray box to the left of Column A and above row 1. This box has a little darker gray triangle pointing to the lower right corner. 2. Click on the "Data" tab and then click "Sort" 3. Check the box "My data has headers" 4. Pull down the menu for "Sort by" and choose the column, such as "Requirement" to get all of the training grouped together by that heading. For example, clicking "EHS Program" will sort the sheet alphabetically by program, and clicking "Work Unit Person Responsible" will sort the list alphabetically by employee name. If you want to sort by more than one category, click "Add Level" and add that second category. 5. Click "Sort" and the data will be sorted.
1/14/2022

## Master CRG List
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Asbestos | Asbestos assessment in equipment (e.g. fume hood liners, ovens, lab bench tops, etc.) | Before maintenance, repair or disposal | Contact EHS before maintenance, repair or disposal; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Asbestos | Asbestos assessment prior to any maintenance, renovation or demolition | Before maintenance, renovation or demolition. | Contact EHS before conducting any work in / on pre-1990 buildings. Exterior renovations such as roofing do not have a date cut-off; contact EHS before any exterior work. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Asbestos | Asbestos awareness training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality
Asbestos - Structural Demolition | Asbestos assessment prior to demolition or removal of structural members within a building | Before demolition or removal of structural members | Contact EHS before demolition or removal of structural members; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Possible sampling and testing fees, depending scope and funding source.
Biosafety | Autoclave quality control | Weekly | Verify effectiveness of sterilization with a biological indicator (Bacillus/Geobacillus spore vials, etc.), and use an indicator such as color-changing autoclave tape with each load to verify adequate sterilization. | N/A | N/A | Labs | ~$250/pack of 25 for spores
Biosafety | Biosafety cabinet annual inspection by third party | Annual | Inspection of biosafety cabinets for proper function must be performed annually by a third party. | Life of equipment | https://ehs.psu.edu/biosafety/biosafety-resources | Labs | Costs vary
Biosafety | Biosafety training | Initial | Training for personnel working with BSL-2 or higher organisms. | Records retained by CITI | https://citi.psu.edu | Labs
Biosafety/Office for Research Protections | Registration and review of Research and Teaching involving Biohazardous and Regulated Materials | Initially and every 3 years | Research and teaching activities involving biohazardous or regulated materials (including "Select Agents") must be reviewed and approved by the Institutional Biosafety Committee (IBC) prior to starting work. Resubmission required every 3 years. See policy RP11 (formerly SY24). | Until superseded (IBC maintains records) | https://www.research.psu.edu/ibc | Labs
Biosafety/Office for Research Protections | Vertebrate animal care and use (IACUC) | Initially and every 3 years | All work with vertebrate animals must be approved by IACUC. | IACUC maintains records | https://www.research.psu.edu/iacuc | Labs
Biosafety/Office for Research Protections | Vertebrate animal care and use (IACUC) training | Initial | Training is required for all employees involved in research with vertebrate animals. | IACUC maintains records | https://citi.psu.edu/ | Labs
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (non-research) | Annual - May | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Bloodborne Pathogens Training | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services
Bloodborne Pathogen | Bloodborne Pathogen training (research) | Annual - August | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | https://citi.psu.edu/ | Researchers working with bloodborne pathogens
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Emergency Evacuations & Fire Drills- Residence Halls | Monthly | Fire Drills are required in Residence Halls monthly when classes are in session | End of calendar year + 7 years | https://policy.psu.edu/policies/sy28 | Residence Life, Police Services, Housing
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Facility Anti-Terrorism Standards | CFATS Inventory | Upon receipt | Upon receipt, update CHIMS database as required by SY39 | Upon receipt of the chemical + 2 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Facility Anti-Terrorism Standards | CFATS Top-Screen Forms | Within 60 Days of Possession | Chemicals of Interest above threshold quantity - must submit Top-Screen Form within 60 days | End of calendar year + 6 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or Waste Management Logbook (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Maintenance, Housing & Food Services, potentially other areas
Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
Confined Space | Confined Space Awareness training | Initial | Training recommended for employees who may work around Confined Spaces but will not be entering those spaces. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Permit | Prior to entry | Permit must be filled out and approved, and hazards must be identified and mitigated, prior to entering confined space | End of calendar year + 1 year | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Training | Initial | Training required for any employee who will be entering a Permit-Required Confined Space | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space inventory | Initial, and updated as needed | Keep an up-to-date list of confined spaces on each campus | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space labeling | Initial | Label all Permit-Required Confined Spaces | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | cost depends on sign type (~$10-150)
Confined Space | Confined Space Rescue | Prior to entry | Prior to entering a Permit-Required Confined Space, a Confined Space Rescue Team must be available and on-call (in-house or county EMS) | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | CS rescue equipment costs at UP
Confined Space | Confined Space Rescue Training | Annual - June | In-house Confined Space Rescue Teams must be trained/refreshed at least once every 12 months | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Inform Contractors | Prior to entry | Inform contractors of confined spaces and any known hazards relevant to their scope of work and remind them that they must comply with OSHA Confined Space standards | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Contractor Safety (OPP) | Contractor safety (construction and non-construction) |  | See OPP contractor/construction safety requirements in Design & Construction standards Division 00. Note: This currently applies only to contractors hired by OPP. | N/A | https://wikispaces.psu.edu/download/attachments/357076600/PSU%20OPP%20Contractor_Safety_Requirements.pdf?version=2&modificationDate=1550257929000&api=v2 | Maintenance, Housing & Food Services, Information Technology
Cranes, Hoists & Slings | Crane/Hoist annual inspection | Annual - May | Annual "periodic" inspection of crane by vendor | Life of equipment | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone | Costs vary by crane type and vendor
Cranes, Hoists & Slings | Crane/hoist monthly inspection | Monthly | Monthly "frequent" inspection of crane by vendor or designated employee | End of calendar year + 3 years | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Daily inspection | Daily | Visual inspection of crane/hoist/sling prior to each use | N/A | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Hands-on user evaluation | Initial | Hands-on evaluation required for Bridge Crane operators | Period of employment in the work unit | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Inventory | Initial, review and update as needed | A listing of all cranes and hoists | Until superseded | Section 8.1.1 of the Crain, Hoist Sling Program Document | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Sling Annual inspection | Annual - May | Annual inspection of sling by Competent Person | Life of equipment | http://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E annual evaluation | Annual - July | Annual evaluation of all employees authorized to perform electrical work (includes LOTO evaluation) | Period of employment in the work unit | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E contractor/host employer meeting | As needed | Document the Contractor / Host Employer meeting. | Superseded/ updated + 1 year |  | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E equipment/task-specific work plans | Initial, review and update as needed | Documentation containing information pertaining to each electrical task and its corresponding PPE requirements shall be maintained by the work unit. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E PPE & equipment inspections | Varies | Electrical safety equipment such as insulating gloves, covers, arc flash suits require inspection. See Appendix G of program for complete list of equipment and frequency | Life of equipment | http://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, could be anyone | Glove inspection ~$40 per pair, every 6 months.
Electrical Safety | Energized Electrical/ NFPA 70E Self-Review of devices | Annual - July | Self-review of electrical devices in laboratories for safety compliance, specifically for machinery >50V. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Engineering, Science labs, Arts | employee time
Electrical Safety | Energized Electrical/ NFPA 70E Training | Every 3 years | Initial classroom training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Energized Electrical/NFPA 70E Arc Flash Training | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E work permit | As needed | Copies of all energized electrical work permits (appendix A) must be provided to both the work unit Safety Officer and the EHS Department upon completion of the task. | End of calendar year + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Environmental / Regulatory Compliance Checklist | Environmental / Regulatory Compliance Checklist Review | Design phase of renovation / construction projects | Project Leaders and Professionals are to complete this form in eBuilder during design phase of OPP projects | N/A |  | OPP
Environmental Emergency Plans | Grease trap clean-out documentation | Varies | Removal of grease from grease traps must be documented. | End of calendar year + 3 years | N/A | Maintenance, Housing & Food Service
Environmental Emergency Plans | Hydraulic elevators (> 55 gallons) inspection | Quarterly | Visual inspection of hydraulic system for leaks | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/elevator_inspection_report.doc | Maintenance, Housing & Food Service | UP: Performed by OPP. Campuses: vendor performs
Environmental Emergency Plans | Oil interceptors & oil/water separators inspection | Semiannually | Inspect oil interceptors and/or oil/water separators at least semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing drums (> 55 gallons) inspection | Monthly | Visual inspection of oil containing drums | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_drum_inspection_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing transformers (> 55 gallons) inspection | Semiannually | Visual inspection of transformer for leaks | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/transformer_inspection_checklist_rev_5-17.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Other oil-filled equipment (> 55 gallons) inspection | Varies | Visual inspection for leaks (see EHERP requirements) | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service, Labs
Environmental Emergency Plans | Review and update EHERP plan | Annual - September | Review and update EHERP as needed (due to personnel or facility changes) and at least annually | Superseded/ updated + 1 year | http://ehs.psu.edu/environmental-emergency-plans/overview | Maintenance, Housing & Food Service, Director of Business Services, Laboratories
Environmental Emergency Plans | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/environmental_hazards_emergency_response_plan_self_audit.docx | Maintenance, Housing & Food Service, and other areas that have a pan
Environmental Emergency Plans | Spill kits | Varies | Maintain and re-stock spill kits in elevator mechanical rooms, laboratories, machine shops, kitchens, storage tank locations, and other areas that require spill response kits. | N/A | http://ehs.psu.edu/environmental-emergency-plans/overview | Any | replacement costs
Environmental Emergency Plans | Spill response training for hazardous materials, oils, and/or storage tanks | Annual | Provide EHERP training to affected employees annually | End of calendar year in which course ends or separation of employment + 30 years |  | Maintenance, Labs, Housing & Food Service
Environmental Emergency Plans | Tier II reporting (SARA) | Due March 1st | Report of any chemical (including road salt and other ice melting products) that exceeds the Threshold Planning Quantity, generally 10,000 pounds or more | Superseded/ outdated + 1 year | https://www.lipatts.pa.gov/Account/Login.aspx | Maintenance
Environmental Emergency Plan / Storage Tanks | PADEP Regulated Storage Tank inspection by PADEP | Varies | Certain PA DEP regulated storage tanks must have an inspection a PA DEP certified inspection as directed on storage tank registration | Life of equipment |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Annual - June | Visual inspection of aboveground storage tanks; this is more comprehensive than the monthly inspection | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/annual_aboveground_storage_tank_inspection_checklist_ehs-064_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Monthly | Visual inspection of aboveground storage tanks; there are two forms, one for fuel/oil storage tanks and one for chemical storage tanks. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_aboveground_storage_tank_inspection_checklist_ehs-062_rev_5-21.docx | Maintenance
https://ehs.psu.edu/sites/ehs/files/monthly_chemical_aboveground_storage_tank_inspection_checklist_ehs-063_rev_5-21.docx
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Every 72 hours | Visual inspection for aboveground storage tanks of 21,000 gallons or greater | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/routine_aboveground_storage_tank_inspection_checklist_ehs-065_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Containment water release inspection | Varies | Visual inspection of rainwater captured by a containment facility prior to release | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/containment_water_release_inspection_checklist_ehs-067_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Observation of tank filling procedures | Varies | Observe and document filling of above- or below-ground tanks | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/product_delivery_observation_form_ehs-068_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | PADEP Regulated Storage Tank Registration | Annual | Annual registration is required for storage tanks that are regulated by PA DEP. There is a fee associated with tank registration. | Until superseded |  | Maintenance | Varies by tank size
Environmental Emergency Plans / Storage Tanks | Underground storage tank annual inspection | Annual - June | Check of underground storage tank monitoring equipment by vendor | Life of equipment |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank facility inspection | Monthly | Underground tank facility general inspection | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_underground_storage_tank_facility_inspection_checklist_ehs-069_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank sump inspections | Monthly | Underground storage sump inspections where no monitor is present must be inspected monthly | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_underground_storage_tank_sunp_inspection_checklist_ehs-070_rev_5-21.docx | Maintenance
Environmental real estate assessment | Environmental due diligence | Prior to leasing / purchasing real estate | If pondering leasing/purchasing/accepting non-PSU real estate, follow Finance and Business Real Estate process. | N/A |  | OPP, campus leadership
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Excavation Safety (OPP) | Excavation Safety PA 1-Call | Prior to work | A PA 1 Call shall be completed prior to any excavation/earth disturbance | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety Training | Annual - March | Competent person excavation training for anyone who performs excavation activities | End of calendar year in which course ends or separation of employment, + 30 years | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety trench inspection | Daily | A competent person shall complete a trench inspection daily, after a rainstorm, or if there is a hazardous condition | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Explosive Management Program | Explosive Permit | Annual | State Permit to purchase explosive materials | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Explosive Management Program | Inventory Count | Annual | Annual physical inventory count of explosive materials | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Explosive Management Program | License Renewal | Every 3 years | Federal license application through ATF | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Explosive Management Program | Magazine Permit | Annual | State license to store explosive materials | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention & Protection | Automatic Fire Suppression Systems | Varies | All Testing / Inspection / Maintenance in accordance with appropriate NFPA standard / FM Global Recommendations for specific system (Sprinkler / Gaseous Agent / Standpipe / Fire Pumps / Backflow Devices etc.) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention/Protection | Automatic Sprinkler System inspection | Monthly | Inspect locked control valves with electronic tamper switches monthly; record pressure readings; investigate if change of 10% or more. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System inspection | Weekly | Inspect locked control valves without electronic tamper switches weekly | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System main drain flow test | Annual | Test main drain flow annually (per NFPA 25) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System tamper switch test | Semiannually | Test Supervisory/Tamper switches semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System water flow alarm test | Quarterly | Test water flow alarms quarterly (per NFPA 25); | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Building Fire Department Connection inspection | Quarterly | Inspect building fire department connections to ensure clear access and operation | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Curb box valve inspection & test | Annual - October | Inspect cover for accessibility; fully close and then fully open valve | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Dry sprinkler/fire suppression systems | Annual - October | Check and maintain low point drains annually prior to freezing weather, and as needed to ensure all water is drained from system piping. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems dry pipe trip test | Annual | Conduct partial trip test annually | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems full flow trip test | Every 3 Years | Conduct full flow trip test | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems inspection | Weekly / Monthly | Inspect valves, ensure locks; inspect gauges and record pressures (weekly without tamper switch, monthly with tamper switch) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems test | Quarterly | Test water flow alarms quarterly (per NFPA 25); test priming water; test low air alarm | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Building Fire Protection Pumps | Weekly or Monthly | Start pump - no flow running (Churn) weekly for Diesel driven, monthly for electric pumps (per NFPA 25) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Building Fire Protection Pumps | Annual | Annual pump inspection and flow test (per NFPA 25) - full flow/performance test and inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire suppression system backflow protection | Annual | Conduct full-flow test in excess of the greatest sprinkler demand | End of calendar year + 3 years | https://ehs.psu.edu/fire-prevention-and-protection/resources | Maintenance, Housing & Food Service | Vendor charge
Fire Prevention/Protection | Emergency generator test | Weekly | Start and verify proper operation | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention/Protection | Emergency lighting / illuminated exit signs | Varies | Monthly activation test to ensure automatic lighting operation; Annual power test | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention/Protection | Fire Alarm System inspection & test | Annual - October | Inspect, maintain, and test fire alarm systems in accordance with NFPA 72 Standard "National Fire Alarm and Signaling Code" by qualified individual (manual pull stations, heat/smoke detectors, back-up batteries, etc.) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire curtain - inspect / test / maintain | Varies | Maintain fire curtain in accordance with NFPA Standard 80. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Theater
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire Hydrant testing | Annual | Flushing/testing of fire hydrant by water authority or campus staff | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Monthly | Monthly inspection / cleaning is required for cooking operations using solid-fuel-burning cooking appliances | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Quarterly | Quarterly inspection / cleaning is required for high-volume or high-smoke/grease cooking operations such as 24-hour cooking, charbroiling, or Wok cooking. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Semiannually - June & December | Cleaning of kitchen cooking exhaust devices (hoods, grease-removal devices, fans, ducts, etc.) at least semi-annually if grease accumulation is observed | Until superseded | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Fire Suppression System Inspection | Semiannually - June & December | Semi-annual inspection, maintenance and testing of fixed fire protection system (per NFPA 17A) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services | Costs vary
Fire Prevention/Protection | Smoke control system - Inspection / testing / maintenance | Varies | Ensure systems are maintained in operable condition and perform as designed. System performance testing/inspection/maintenance in accordance with appropriate National Fire Protection Association (NFPA) standard for type system. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire safety - Vital Building Information | Annually | Pesticide storage buildings, if they catch fire, should not be extinguished with water as runoff would be toxic. Smoke can also be toxic. EHERP should include this information, and building should have appropriate signage. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Agriculture
Fire Prevention/Protection | Resident RA/GA training in fire safety | Annual - August | Fire safety training including fire extinguisher use, building evacuation, and fire prevention, for Resident Advisors, Resident Directors, and Graduate Advisors living in PSU housing | Residence Life Maintains | http://ehs.psu.edu/fire-prevention-and-protection/overview | Housing / Residence Life, Student Affairs
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hazardous Materials Shipping | Hazardous Materials/Dangerous Goods Shipping Training | Every 2 Years | Individuals who ship hazardous materials (biological, chemical, radioactive, and/or waste) and sign paperwork must receive DOT/IATA and/or NRC training every other year. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Maintenance, Janitorial, Housing & Food Service, Police Services
Hazmat shipping: Import/Export permits (Ethics & Compliance) | HazMat Shipments - Import/Export Permits (TSCA) | Prior to shipping internationally | Refer to Ethics & Compliance website and the EHS Hazardous Materials shipping program for information on importing or exporting hazardous materials | EHS retains forms | https://universityethics.psu.edu/export-compliance | Any
Hearing Conservation | Medical Surveillance - hearing tests | Annual | Annual hearing test for employees in Hearing Conservation Program | Records kept by Occupational Medicine | http://ehs.psu.edu/hearing-conservation/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Occ Med at UP; contracted providers at campuses.
Hearing Conservation | Training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Hearing Conservation | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring, exposure monitoring, and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except Classroom and Office
Industrial Hygiene / Chemical Hygiene / Lab Safety / Biosafety | Commissioning of fume hoods and biosafety cabinets | Initial | Commissioning of fume hoods by 3rd party (test reports) prior to first performance test and use | Archive/Storage by Project Team; Biosafety Cabinets additionally by User | OPP Design and Construction Standards- D&C Standards (23.00.10.12) Lab Vent Systems | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre | Costs vary by hood type and vendor
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Industrial Hygiene/ Laboratory Safety/ Chemical Hygiene | Annual fume hood testing | Annual - as scheduled | Transitioned to OPP | Archived by EHS, historically, transitioned to OPP for U/Park |  | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety/ Chemical Hygiene | Carcinogen hazard assessment and substance-specific control plans, as applicable, where determined necessary by initial exposure assessment | Initial and update annually | Wherever determined necessary by exposure level, or where required by OSHA regulation, substance-specific control plans shall be prepared. Use of carcinogens (including but not limited to materials regulated by individual OSHA substance-specific standards (e.g. formaldehyde, beryllium, arsenic, hexavalent chromium, cadmium, benzene, etc.) and similar highly hazardous materials must undergo a hazard assessment prior to work commencing. Engineering controls shall be used whenever possible. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/forms | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene/ Laboratory Safety/ Chemical Hygiene | Gas monitoring & alarms | As needed | Where gas monitors are installed or needed, follow procedures outlined in the Gas Monitoring Program. | See program | https://ehs.psu.edu/sites/ehs/files/gas_monitoring_program_-_final.docx | Labs, Engineering, Maintenance | Monitoring devices
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Develop & update Standard Operating Procedures (SOPs) | Initial | Develop SOPs for hazardous substances, equipment, and processes. Review annually as part of the USP review and update as necessary | Life of equipment | http://ehs.psu.edu/sops | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory & Research Safety Plan / Unit Specific Plan preparation and review | Initial, review and update as needed | Prepare a Unit Specific safety plan for each laboratory, and update annually | Until superseded/ updated + 1 year | http://ehs.psu.edu/sites/ehs/files/unit_specific_plan_form_template_added_ghs.doc | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory closeout (not moving anywhere) consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for closing a lab down permanently. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_closeout_certification.docx | Academics/Research
Laboratory Safety | Laboratory move to another institution - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab externally (outside PSU. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_external_move_guidelines.docx | Academics/Research
Laboratory Safety | Laboratory move within Penn State - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab internally (to other PSU space). | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_internal_move_guidelines.docx | Academics/Research
Laboratory Safety | Preserved specimens - hazard assessment | Prior to moving, handling, or disposal | Refer to the Laboratory Safety and Research Plan (line item 177) - content provided at LRSP Section 9.4. | N/A |  | Academics/Research, Museums
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety | Self-inspection | Annual - January | Laboratory self-inspection | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/lab_self_inspection_2022_-_form.docx | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (initial) | Initial | All laboratory personnel must complete initial Laboratory Safety training prior to working in the lab | End of calendar year in which course ends or separation of employment + 30 years | EHS - Initial Laboratory & Research Safety Training - University Park | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (refresher) | Annual - August | All laboratory personnel must complete Laboratory Safety refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS – Laboratory and Research Safety Refresher Training - All Locations | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Laboratory Safety/Office of Research Protections | Controlled substances - DEA registration | Initial | All researchers working with controlled substances must work with ORP to obtain and maintain their DEA registration | NA | https://www.research.psu.edu/controlsubs | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety; OPP | Pressure vessel inspection | Annual | Annual inspection of pressure vessels (autoclaves, boilers, etc.) by Labor & Industry. Managed by Risk Management through FM Global. | Keep current version | N/A | OPP, Maintenance, Laboratories
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead in building materials | Assessment of Lead in other building materials (flashing, window camings, etc.) | Prior to demolition / work that affects lead-containing material | Contact EHS prior to any work that could affect lead-containing materials. This includes but is not limited to: lead flashing, window camings, lead-lined walls for X-ray suites, etc. | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, Residence Hall Housekeeping, OPP PMs, PCs, Designers | sampling and testing fees vary
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Lead Paint | Assessment of lead paint in all maintenance, renovation or demolition that affects paint | Before maintenance, renovation or demolition that affects paint | Follow EHS / OPP Lead Paint Procedures | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP | Possible sampling and testing fees, depending scope and funding source.
Lead Paint | Assessment of lead paint in pre-1978 residential housing (non-undergraduate) and child-occupied facilities (e.g. daycare) | Before maintenance, renovation or demolition that affects paint | Contact EHS prior to any work that could affect paint. | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Lead Paint | Lead paint awareness training | Prior to initial exposure | Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality
Lockout/Tagout | LOTO Affected Personnel Training | Initial | Initial training for employees who do not perform LOTO but may be affected by equipment that is LOTO'd | End of calendar year in which course ends or separation of employment + 30 years | EHS - Lockout/Tagout Affected Employee Training | Maintenance, could be anyone
Lockout/Tagout | LOTO contractor notification forms | Prior to contractor beginning work | Work units must exchange LOTO procedures with contractors servicing/maintaining PSU equipment that requires LOTO. This form documents that information exchange. | End of calendar year + 1 year | https://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Lockout/Tagout | LOTO evaluation | Annual - July | Annual evaluation of all employees authorized to use Lockout/Tagout procedures | Period of employment in the work unit | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO lock removal form | As needed | Documentation of lock removal by anyone other than designated employee to whom lock is assigned | End of calendar year + 1 year |  | Maintenance, could be anyone
Lockout/Tagout | LOTO procedures | Initial and update as needed | Documented LOTO procedure is required for equipment with multiple energy sources | Life of equipment | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO training | Initial | Initial training for employees who perform Lockout/Tagout | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | https://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Mobile Crane Safety (OPP) | Crane Inspection | Prior to each use of equipment | Pre-use Inspection using the NCCCO Mobile Crane Inspection Form | End of calendar year + 4 years | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | Crane Inspection | Annual | Annual inspection of sling by 3rd Party | Life of equipment | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | Crane Operator Training | Every 5 Years | Written Exam and Hands-on evaluation required for Crane operators | End of calendar year in which course ends or separation of employment + 30 years | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | PA One Call prior to Crane setup | Prior to each set-up of equipment | Complete Pa One Call prior to crane set up | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | Rigger 1 Training | Every 5 Years | Written Exam and Hands-on evaluation required for Rigger 1 | End of calendar year in which course ends or separation of employment + 30 years | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | Rigging Inspection | Prior to each use of equipment | Follow EHS/OPP Chain/Sling Inspection Program | End of calendar year + 4 years | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Multiple EHS programs | Boating Safety Training | Initial | Boating safety training is required by PA Fish & Boat Commission | End of calendar year in which course ends or separation of employment + 30 years | https://www.boat-ed.com/pennsylvania/ | Academics/Research
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Clinical Human Research (IRB) protocol review | Prior to starting research project | IRB determines that clinical research protocols involving human subjects may require individual approval by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/qualitymanagement | Labs/research
Office for Research Protections | Diving Safety (research) certification | Initial | Scientific divers must be trained/certified | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety (research) dive log | After each dive | Scientific divers must submit a log of each dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety Plan review (research) | Prior to dive | Diving Safety Plan must be approved prior to each scientific dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Human Subjects Research (IRB) plan review | Prior to starting research project | All research involving human subjects must be approved by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/irb | Labs/research
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
OPP / Athletics | Building Code (PA) including bleacher safety | Every 3 years | Bleachers must be inspected by an external party at least once every 3 years per PA Dep't of Labor & Industry | Life of equipment | N/A | Athletics, Student Affairs | External inspector fee varies
OPP / Construction fencing | Construction fencing (Temporary & Worksite Barricading) | Duration of construction | Maintain appropriate fencing/barricading of construction worksites as outlined in OPP Design & Construction standard 01 50 00. | N/A | https://wikispaces.psu.edu/display/OPPDCS/01+50+00+TEMPORARY+FACILITIES+AND+CONTROLS | Maintenance, H&FS
OPP / Industrial Hygiene | Paint spraying operations hazard assessment | Initial and update annually | Paint spraying operations shall undergo hazard assessment prior to work commencing. Spray booths or other engineering controls may be required. | End of calendar year + 1 year | N/A | OPP | employee time; potentially installation of ventilation hoods
PCB building materials | Assess for PCBs prior to all maintenance, renovation or demolition in / on pre-1980 facilities | Before maintenance, renovation or demolition. | Contact EHS before conducting maintenance, renovations or demolition in / on pre-1980 buildings. | Records retained by EHS | N/Ahttps://ehs.psu.edu/PCB-Containing%20Building%20Material%20Management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Pest Management | Integrated Pest Management plan review | Annually | If you have an Integrated Pest Management Plan, review it annually to ensure it is up to date and that program is being followed as provided by the plan | Until superseded/ updated + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-integrated-pest-management | Maintenance, Housing and Food Services
Pesticides | Application records | Varies | Pesticide application records must be kept for the past 3 years. | Date of application + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Eyewash | Prior to use | For pesticides being mixed from concentrates, a flowing eyewash must be present in the area where the pesticide is mixed. If the pesticide label says eye protection is required, then the applicators must carry bottled eyewash with them.
Pesticides | Eyewash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Inventory | Annual - January | Annual pesticide inventory (in CHIMs) | Date of acquisition + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | License | Annual | Copies of the annual Certified Applicator License and the Pesticide Business License must be up-to-date and available. | Until superseded | N/A | Maintenance, Labs/farms/research using pesticides
Pesticides | Pesticide storage area inspection | Monthly | Inspect pesticide storage area | End of calendar year + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/pesticide_facility_annual_self_audit_0.docx | Maintenance, Housing & Food Service, Labs/farms/research using pesticides
Pesticides | Worker Protection Standard Training | Annual | All employees who are not certified applicators and who work in areas where pesticides are used for agricultural applications, including greenhouses, must take annual training. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs/farms/research using pesticides
Powered Industrial Trucks (forklifts) | PIT annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone | External inspector fee varies
Powered Industrial Trucks (forklifts) | PIT daily inspection | Daily | Documented by operator | End of calendar year + 1 year | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT hands-on user evaluation | Every 3 years | Hands-on evaluation required for PIT (forklift) operators | Period of employment in the work unit | https://ehs.psu.edu/pit/forms | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT inventory | Initial, review and update as needed | Each work unit is responsible for keeping a list of all PITs within the work unit. | Until superseded |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT repair records | As needed | Retain all repair records | Life of equipment |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT user training | Initial | Initial classroom & hands-on training for users of PITs (forklifts) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Powered Industrial Truck (Forklift) Training | Maintenance, could be anyone
Process Safety Management (PSM) | Contractor Qualification Assessment | Annual | Pre-Qualification Data Reviewed by EHS | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors bidding on projects relating to PSM Covered Process Equipment
Process Safety Management (PSM) | Hazardous Line Opening Permit Training | Initial | Personnel who open PSM Covered Process equipment (e.g., pipes, vessels, tanks, etc.) must be trained on the Hazardous Line Opening Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Hazardous Line Opening Requirements | As needed | A Hazardous Line Opening Permit must be completed by PSM Authorized Employees when opening any PSM Covered equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | PSM Awareness & Contractor Responsibilities Training | Annual | Annual PSM Awareness and Contractor Responsibilities | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors working in or around Covered Process Areas
Process Safety Management (PSM) | PSM Steering Committee - Review | Annual | At least annually review the progress (e.g., metrics, incidents, etc.) and performance of PSM program | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, College of Ag, Athletics, Animal Resource Program, Risk Management
Process Safety Management (PSM) | Safe Work Permit Requirements | As needed | A Safe Work Permit must be completed for non-routine maintenance activities associated with PSM Covered Process Equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Safe Work Permit Training | Initial | Personnel who perform maintenance activities on PSM Covered Process Equipment must be trained on the Safe Work Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Radiation | Inventory Update | Annual - February | Annual inventory update | Date of acquisition + 1 year | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive material safety training | Annual | All users of radioactive materials must complete Initial training prior to using material, and refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS-Radionuclide Safety Education | Labs using Radioactive Materials
Radiation | Radioactive Material Survey | Daily | Survey after each use of radioactive material, decontaminate as needed | End of calendar year + 3 years | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive materials Lab Survey | Quarterly or Monthly | EHS conducts quarterly or monthly contamination survey of radiation-using labs | Records retained by EHS. Where representing exposure, maintain 30 years, or until license termination, whichever is longer. | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Refrigerant | Annual self-audit for appliance owners | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self-audit_for_appliance_owners.docx | Maintenance, Housing & Foods
Refrigerant | Annual self-audit for service providers | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self_audit_for_service_providers.docx | Maintenance, Housing & Foods
Refrigerant | Appliance Inventory | Annual - January | Inventory of all refrigeration units containing 50 or more pounds of circuit | Until superseded | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Certification | Initial | Maintain certification(s) for employees who use refrigerants | Period of employment in the work unit + 3 years | N/A | Maintenance, Housing & Foods
Refrigerant | Leak Rate Calculations | Varies | For all appliances containing 50 pounds or more of refrigerant in a circuit, leak rates must be calculated each time refrigerant is added. There is a spreadsheet which performs these calculations. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Refrigerant Inventory | As needed | Keep a log of all refrigerant usage from purchase to return for reclamation | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Service records | Varies | Maintain required service records and submit them to the appliance owner, including all records referring to refrigerant used, removed, or reclaimed. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Regulated Medical Waste | Regulated Medical Waste Pickup (Campuses) | Quarterly or more often as needed | Regulated medical waste cannot remain on campus more than 90 days. Details on handling are in policy SY29. | End of calendar year + 2 years | http://ehs.psu.edu/infectious-waste-management/overview | Laboratories, Nurses
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Theater Rigging | Theater Rigging Inspection (annual) | Annual - January | Documented inspection by a Competent Inspector is required annually | Life of equipment | https://ehs.psu.edu/theatre-rigging/forms | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (Third Party) | Every 3 years | Documented inspection by a third party (outside vendor) is required every 3 years. | Life of equipment | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (visual) | Prior to Use | Rigging must be visually inspected before each use | N/A | https://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspector training | Initial | Training is required for Competent inspectors of theatrical rigging. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Repair Records | As needed | Retain all repair records | Life of equipment |  | Maintenance, Theater Department faculty/staff
Visual Arts | Visual Arts Safety Plan - Unit Specific Plan | Initial, update annually: August | Prepare a Unit Specific safety plan for each art studio | Superseded/ updated + 1 year | http://ehs.psu.edu/sites/ehs/files/visual_arts_unit_specific_plan_2-14.pdf | Art department faculty, students, staff
Visual Arts | Visual Arts Safety Training (initial) | Initial | Initial Visual Arts Safety training is required for all personnel working in an Art studio | End of calendar year in which course ends or separation of employment + 30 years | EHS - Visual Arts Safety Initial Training - UP | Art department faculty, students, staff
Visual Arts | Visual Arts Safety Training (refresher) | Annual - August | Annual refresher training is required for all personnel working in an Art studio. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Visual Arts Safety Refresher Training - All Locations | Art department faculty, students, staff
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Ag Science
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Asbestos | Asbestos assessment in equipment (e.g. fume hood liners, ovens, lab bench tops, etc.) | Before maintenance, repair or disposal | Contact EHS before maintenance, repair or disposal; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Biosafety | Autoclave quality control | Weekly | Verify effectiveness of sterilization with a biological indicator (Bacillus/Geobacillus spore vials, etc.), and use an indicator such as color-changing autoclave tape with each load to verify adequate sterilization. | N/A | N/A | Labs | ~$250/pack of 25 for spores
Biosafety | Biosafety cabinet annual inspection by third party | Annual | Inspection of biosafety cabinets for proper function must be performed annually by a third party. | Life of equipment | https://ehs.psu.edu/biosafety/biosafety-resources | Labs | Costs vary
Biosafety | Biosafety training | Initial | Training for personnel working with BSL-2 or higher organisms. | Records retained by CITI | https://citi.psu.edu | Labs
Biosafety/Office for Research Protections | Registration and review of Research and Teaching involving Biohazardous and Regulated Materials | Initially and every 3 years | Research and teaching activities involving biohazardous or regulated materials (including "Select Agents") must be reviewed and approved by the Institutional Biosafety Committee (IBC) prior to starting work. Resubmission required every 3 years. See policy RP11 (formerly SY24). | Until superseded (IBC maintains records) | https://www.research.psu.edu/ibc | Labs
Biosafety/Office for Research Protections | Vertebrate animal care and use (IACUC) | Initially and every 3 years | All work with vertebrate animals must be approved by IACUC. | IACUC maintains records | https://www.research.psu.edu/iacuc | Labs
Biosafety/Office for Research Protections | Vertebrate animal care and use (IACUC) training | Initial | Training is required for all employees involved in research with vertebrate animals. | IACUC maintains records | https://citi.psu.edu/ | Labs
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (research) | Annual - August | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | https://citi.psu.edu/ | Researchers working with bloodborne pathogens
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Facility Anti-Terrorism Standards | CFATS Inventory | Upon receipt | Upon receipt, update CHIMS database as required by SY39 | Upon receipt of the chemical + 2 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Facility Anti-Terrorism Standards | CFATS Top-Screen Forms | Within 60 Days of Possession | Chemicals of Interest above threshold quantity - must submit Top-Screen Form within 60 days | End of calendar year + 6 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or Waste Management Logbook (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Maintenance, Housing & Food Services, potentially other areas
Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
Confined Space | Confined Space Awareness training | Initial | Training recommended for employees who may work around Confined Spaces but will not be entering those spaces. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Permit | Prior to entry | Permit must be filled out and approved, and hazards must be identified and mitigated, prior to entering confined space | End of calendar year + 1 year | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Training | Initial | Training required for any employee who will be entering a Permit-Required Confined Space | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space inventory | Initial, and updated as needed | Keep an up-to-date list of confined spaces on each campus | Until superseded | https://ehs.psu.edu/waste-disposal | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space labeling | Initial | Label all Permit-Required Confined Spaces | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | cost depends on sign type (~$10-150)
Confined Space | Confined Space Rescue | Prior to entry | Prior to entering a Permit-Required Confined Space, a Confined Space Rescue Team must be available and on-call (in-house or county EMS or provider) | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | CS rescue equipment costs at UP
Confined Space | Confined Space Rescue Training | Annual - June | In-house Confined Space Rescue Teams must be trained/refreshed at least once every 12 months | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Inform Contractors | Prior to entry | Inform contractors of confined spaces and any known hazards relevant to their scope of work and remind them that they must comply with OSHA Confined Space standards | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Cranes, Hoists & Slings | Crane/Hoist annual inspection | Annual - May | Annual "periodic" inspection of crane by vendor | Life of equipment | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone | Costs vary by crane type and vendor
Cranes, Hoists & Slings | Crane/hoist monthly inspection | Monthly | Monthly "frequent" inspection of crane by vendor or designated employee | End of calendar year + 3 years | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Daily inspection | Daily | Visual inspection of crane/hoist/sling prior to each use | N/A | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Hands-on user evaluation | Initial | Hands-on evaluation required for Bridge Crane operators | Period of employment in the work unit | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Inventory | Initial, review and update as needed | A listing of all cranes and hoists | Until superseded | Section 8.1.1 of the Crain, Hoist Sling Program Document | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Sling Annual inspection | Annual - May | Annual inspection of sling by Competent Person | Life of equipment | http://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Environmental / Regulatory Compliance Checklist | Environmental / Regulatory Compliance Checklist Review | Design phase of renovation / construction projects | Project Leaders and Professionals are to complete this form in eBuilder during design phase of OPP projects | N/A |  | OPP
Environmental Emergency Plan / Storage Tanks | PADEP Regulated Storage Tank inspection by PADEP | Varies | Certain PA DEP regulated storage tanks must have an inspection a PA DEP certified inspection as directed on storage tank registration | Life of equipment | http://www.dep.pa.gov/Business/Land/Tanks/Pages/Forms-and-Applications.aspx | Maintenance
Environmental Emergency Plans | Oil interceptors & oil/water separators inspection | Semiannually | Inspect oil interceptors and/or oil/water separators at least semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing drums (> 55 gallons) inspection | Monthly | Visual inspection of oil containing drums | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_drum_inspection_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing transformers (> 55 gallons) inspection | Semiannually | Visual inspection of transformer for leaks | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/transformer_inspection_checklist_rev_5-17.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Other oil-filled equipment (> 55 gallons) inspection | Varies | Visual inspection for leaks (see EHERP requirements) | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service, Labs
Environmental Emergency Plans | Review and update EHERP plan | Annual - September | Review and update EHERP as needed (due to personnel or facility changes) and at least annually | Superseded/ updated + 1 year | http://ehs.psu.edu/environmental-emergency-plans/overview | Maintenance, Housing & Food Service, Director of Business Services, Laboratories
Environmental Emergency Plans | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/environmental_hazards_emergency_response_plan_self_audit.docx | Maintenance, Housing & Food Service, and other areas that have a pan
Environmental Emergency Plans | Spill kits | Varies | Maintain and re-stock spill kits in elevator mechanical rooms, laboratories, machine shops, kitchens, storage tank locations, and other areas that require spill response kits. | N/A | http://ehs.psu.edu/environmental-emergency-plans/overview | Any | replacement costs
Environmental Emergency Plans | Spill response training for hazardous materials, oils, and/or storage tanks | Annual | Provide EHERP training to affected employees annually | End of calendar year in which course ends or separation of employment + 30 years |  | Maintenance, Labs, Housing & Food Service
Environmental Emergency Plans | Tier II reporting (SARA) | Due March 1st | Report of any chemical (including road salt and other ice melting products) that exceeds the Threshold Planning Quantity, generally 10,000 pounds or more | Superseded/ outdated + 1 year | https://www.lipatts.pa.gov/Account/Login.aspx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Annual - June | Visual inspection of aboveground storage tanks; this is more comprehensive than the monthly inspection. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/annual_aboveground_storage_tank_inspection_checklist_ehs-064_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Monthly | Visual inspection of aboveground storage tanks; there are two forms, one for fuel/oil storage tanks and one for chemical storage tanks. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_aboveground_storage_tank_inspection_checklist_ehs-062_rev_5-21.docx | Maintenance
https://ehs.psu.edu/sites/ehs/files/monthly_chemical_aboveground_storage_tank_inspection_checklist_ehs-063_rev_5-21.docx
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Every 72 hours | Visual inspection for aboveground storage tanks of 21,000 gallons or greater | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/routine_aboveground_storage_tank_inspection_checklist_ehs-065_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Containment water release inspection | Varies | Visual inspection of rainwater captured by a containment facility prior to release | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/containment_water_release_inspection_checklist_ehs-067_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Observation of tank filling procedures | Varies | Observe and document filling of above- or below-ground tanks | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/product_delivery_observation_form_ehs-068_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | PADEP Regulated Storage Tank Registration | Annual | Certain PA DEP Regulated storage tanks must have an inspection by a PA DEP certified inspection as directed on storage tank registration. | Until superseded |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground storage tank annual inspection | Annual - June | Check of underground storage tank monitoring equipment by vendor | Life of equipment |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank facility inspection | Monthly | Underground tank facility general inspection | Varies by tank size |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank sump inspections | Monthly | Underground storage sump inspections where no monitor is present must be inspected monthly | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_underground_storage_tank_sunp_inspection_checklist_ehs-070_rev_5-21.docx | Maintenance
Environmental real estate assessment | Environmental due diligence | Prior to leasing / purchasing real estate | If pondering leasing/purchasing/accepting non-PSU real estate, follow Finance and Business Real Estate process. | N/A |  | OPP, campus leadership
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Excavation Safety (OPP) | Excavation Safety PA 1-Call | Prior to work | A PA 1 Call shall be completed prior to any excavation/earth disturbance | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety Training | Annual - March | Competent person excavation training for anyone who performs excavation activities | End of calendar year in which course ends or separation of employement, + 30 years | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety trench inspection | Daily | A competent person shall complete a trench inspection daily, after a rainstorm, or if there is a hazardous condition | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hazardous Materials Shipping | Hazardous Materials/Dangerous Goods Shipping Training | Every 2 Years | Individuals who ship hazardous materials (biological, chemical, radioactive, and/or waste) and sign paperwork must receive DOT/IATA and/or NRC training every other year. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Maintenance, Janitorial, Housing & Food Service, Police Services
Hazmat shipping: Import/Export permits (Ethics & Compliance) | HazMat Shipments - Import/Export Permits (TSCA) | Prior to shipping internationally | Refer to Ethics & Compliance website and the EHS Hazardous Materials shipping program for information on importing or exporting hazardous materials | EHS retains forms | https://universityethics.psu.edu/export-compliance | Any
Hearing Conservation | Medical Surveillance - hearing tests | Annual | Annual hearing test for employees in Hearing Conservation Program | Records kept by Occupational Medicine | http://ehs.psu.edu/hearing-conservation/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Occ Med at UP; contracted providers at campuses.
Hearing Conservation | Training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Hearing Conservation | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring, exposure monitoring, and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene / Chemical Hygiene / Lab Safety / Biosafety | Commissioning of fume hoods and biosafety cabinets | Initial | Commissioning of fume hoods by 3rd party( test reports) prior to first performance test and use | Archive/Storage by Project Team; Biosafety Cabinets additionally by User | OPP Design and Construction Standards- D&C Standards (23.00.10.12) Lab Vent Systems | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre | Costs vary by hood type and vendor
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Industrial Hygiene/ Laboratory Safety / Chemical Hygiene | Annual fume hood testing | Annual - as scheduled | Transitioned to OPP | Archived by EHS historically, transitioned to OPP for U/Park |  | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene/ Laboratory Safety/ Chemical Hygiene | Carcinogen hazard assessment and substance-specific control plans, as applicable, where determined necessary by initial exposure assessment | Initial and update annually | Wherever determined necessary by exposure level, or where required by OSHA regulation, substance-specific control plans shall be prepared. Use of carcinogens (including but not limited to materials regulated by individual OSHA substance-specific standards (e.g. formaldehyde, beryllium, arsenic, hexavalent chromium, cadmium, benzene, etc.) and similar highly hazardous materials must undergo a hazard assessment prior to work commencing. Engineering controls shall be used whenever possible. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/forms | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene/ Laboratory Safety/ Chemical Hygiene | Gas monitoring & alarms | As needed | Where gas monitors are installed or needed, follow procedures outlined in the Gas Monitoring Program. | See program | https://ehs.psu.edu/sites/ehs/files/gas_monitoring_program_-_final.docx | Labs, Engineering, Maintenance | Monitoring devices
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Develop & update Standard Operating Procedures (SOPs) | Initial | Develop SOPs for hazardous substances, equipment, and processes. Review annually as part of the USP review and update as necessary | Life of equipment | http://ehs.psu.edu/sops | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory & Research Safety Plan / Unit Specific Plan preparation and review | Initial, review and update as needed | Prepare a Unit Specific safety plan for each laboratory, and update annually | Until superseded/ updated + 1 year | http://ehs.psu.edu/sites/ehs/files/unit_specific_plan_form_template_added_ghs.doc | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory closeout (not moving anywhere) consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for closing a lab down permanently. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_closeout_certification.docx | Academics/Research
Laboratory Safety | Laboratory move to another institution - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab externally (outside PSU. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_external_move_guidelines.docx | Academics/Research
Laboratory Safety | Laboratory move within Penn State - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab internally (to other PSU space). | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_internal_move_guidelines.docx | Academics/Research
Laboratory Safety | Preserved specimens - hazard assessment | Prior to moving, handling, or disposal | Refer to the Laboratory Safety and Research Plan (line item 177) - content provided at LRSP Section 9.4. | N/A |  | Academics/Research, Museums
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety | Self-inspection | Annual - January | Laboratory self-inspection | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/lab_self_inspection_2022_-_form.docx | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (initial) | Initial | All laboratory personnel must complete initial Laboratory Safety training prior to working in the lab | End of calendar year in which course ends or separation of employment + 30 years | EHS - Initial Laboratory & Research Safety Training - University Park | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (refresher) | Annual - August | All laboratory personnel must complete Laboratory Safety refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS – Laboratory and Research Safety Refresher Training - All Locations | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Laboratory Safety/Office of Research Protections | Controlled substances - DEA registration | Initial | All researchers working with controlled substances must work with ORP to obtain and maintain their DEA registration | NA | https://www.research.psu.edu/controlsubs | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety; OPP | Pressure vessel inspection | Annual | Annual inspection of pressure vessels (autoclaves, boilers, etc.) by Labor & Industry. Managed by Risk Management through FM Global. | Keep current version | N/A | OPP, Maintenance, Laboratories
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Lockout/Tagout | LOTO Affected Personnel Training | Initial | Initial training for employees who do not perform LOTO but may be affected by equipment that is LOTO'd | End of calendar year in which course ends or separation of employment + 30 years | EHS - Lockout/Tagout Affected Employee Training | Maintenance, could be anyone
Lockout/Tagout | LOTO contractor notification forms | Prior to contractor beginning work | Work units must exchange LOTO procedures with contractors servicing/maintaining PSU equipment that requires LOTO. This form documents that information exchange. | End of calendar year + 1 year | https://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Lockout/Tagout | LOTO evaluation | Annual - July | Annual evaluation of all employees authorized to use Lockout/Tagout procedures | Period of employment in the work unit | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO lock removal form | As needed | Documentation of lock removal by anyone other than designated employee to whom lock is assigned | End of calendar year + 1 year |  | Maintenance, could be anyone
Lockout/Tagout | LOTO procedures | Initial and update as needed | Documented LOTO procedure is required for equipment with multiple energy sources | Life of equipment | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO training | Initial | Initial training for employees who perform Lockout/Tagout | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | http://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Diving Safety (research) certification | Initial | Scientific divers must be trained/certified | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety (research) dive log | After each dive | Scientific divers must submit a log of each dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety Plan review (research) | Prior to dive | Diving Safety Plan must be approved prior to each scientific dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Pest Management | Integrated Pest Management plan review | Annually | If you have an Integrated Pest Management Plan, review it annually to ensure it is up to date and that program is being followed as provided by the plan. | Until superseded/ updated + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-integrated-pest-management | Maintenance, Housing and Food Services
Pesticides | Application records | Varies | Pesticide application records must be kept for the past 3 years. | Date of application + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Eyewash | Prior to use | For pesticides being mixed from concentrates, a flowing eyewash must be present in the area where the pesticide is mixed. If the pesticide label says eye protection is required, then the applicators must carry bottled eyewash with them.
Pesticides | Eyewash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Inventory | Annual - January | Annual pesticide inventory (in CHIMs) | Date of acquisition + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | License | Annual | Copies of the annual Certified Applicator License and the Pesticide Business License must be up-to-date and available. | Until superseded | N/A | Maintenance, Labs/farms/research using pesticides
Pesticides | Pesticide storage area inspection | Monthly | Inspect pesticide storage area | End of calendar year + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/pesticide_facility_annual_self_audit_0.docx | Maintenance, Housing & Food Service, Labs/farms/research using pesticides
Pesticides | Worker Protection Standard Training | Annual | All employees who are not certified applicators and who work in areas where pesticides are used for agricultural applications, including greenhouses, must take annual training. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs/farms/research using pesticides
Powered Industrial Trucks (forklifts) | PIT repair records | As needed | Retain all repair records | Life of equipment |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone | External inspector fee varies
Powered Industrial Trucks (forklifts) | PIT daily inspection | Daily | Documented by operator | End of calendar year + 1 year | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT hands-on user evaluation | Every 3 years | Hands-on evaluation required for PIT (forklift) operators | Period of employment in the work unit | https://ehs.psu.edu/pit/forms | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT inventory | Initial, review and update as needed | Each work unit is responsible for keeping a list of all PITs within the work unit. | Until superseded |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT user training | Initial | Initial classroom & hands-on training for users of PITs (forklifts) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Powered Industrial Truck (Forklift) Training | Maintenance, could be anyone
Radiation | Inventory Update | Annual - February | Annual inventory update | Date of acquisition + 1 year | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive material safety training | Annual | All users of radioactive materials must complete Initial training prior to using material, and refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS-Radionuclide Safety Education | Labs using Radioactive Materials
Radiation | Radioactive Material Survey | Daily | Survey after each use of radioactive material, decontaminate as needed | End of calendar year + 3 years | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive materials Lab Survey | Quarterly or Monthly | EHS conducts quarterly or monthly contamination survey of radiation-using labs | Records retained by EHS. Where representing exposure, maintain 30 years, or until license termination, whichever is longer. | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Regulated Medical Waste | Regulated Medical Waste Pickup (Campuses) | Quarterly or more often as needed | Regulated medical waste cannot remain on campus more than 90 days. Details on handling are in policy SY29. | End of calendar year + 2 years | http://ehs.psu.edu/infectious-waste-management/overview | Laboratories, Nurses
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Art Studios
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Asbestos | Asbestos assessment in equipment (e.g. fume hood liners, ovens, lab bench tops, etc.) | Before maintenance, repair or disposal | Contact EHS before maintenance, repair or disposal; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or Waste Management Logbook (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | N/A | Maintenance, Housing & Food Services, potentially other areas
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring, exposure monitoring, and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene / Chemical Hygiene / Lab Safety / Biosafety | Commissioning of fume hoods and biosafety cabinets | Initial | Commissioning of fume hoods by 3rd party (test reports) prior to first performance test and use | Archive/Storage by Project Team; Biosafety Cabinets additionally by User | OPP Design and Construction Standards- D&C Standards (23.00.10.12) Lab Vent Systems | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre | Costs vary by hood type and vendor
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Industrial Hygiene/ Laboratory Safety / Chemical Hygiene | Annual fume hood testing | Annual - as scheduled | Transitioned to OPP | Archived by EHS, historically, transitioned to OPP for U/Park |  | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene/ Laboratory Safety / Chemical Hygiene | Carcinogen hazard assessment and substance-specific control plans, as applicable, where determined necessary by initial exposure assessment | Initial and update annually | Wherever determined necessary by exposure level, or where required by OSHA regulation, substance-specific control plans shall be prepared. Use of carcinogens (including but not limited to materials regulated by individual OSHA substance-specific standards (e.g. formaldehyde, beryllium, arsenic, hexavalent chromium, cadmium, benzene, etc.) and similar highly hazardous materials must undergo a hazard assessment prior to work commencing. Engineering controls shall be used whenever possible. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/forms | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Develop & update Standard Operating Procedures (SOPs) | Initial | Develop SOPs for hazardous substances, equipment, and processes. Review annually as part of the USP review and update as necessary | Life of equipment | http://ehs.psu.edu/sops | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | http://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Theater Rigging | Theater Rigging Inspection (annual) | Annual - January | Documented inspection by a Competent Inspector is required annually | Life of equipment | https://ehs.psu.edu/theatre-rigging/forms | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (Third Party) | Every 3 years | Documented inspection by a third party (outside vendor) is required every 3 years. | Life of equipment | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (visual) | Prior to Use | Rigging must be visually inspected before each use | N/A | https://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspector training | Initial | Training is required for Competent inspectors of theatrical rigging. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Repair Records | As needed | Retain all repair records | Life of equipment |  | Maintenance, Theater Department faculty/staff
Visual Arts | Visual Arts Safety Plan - Unit Specific Plan | Initial, update annually: August | Prepare a Unit Specific safety plan for each art studio | Superseded/ updated + 1 year | http://ehs.psu.edu/sites/ehs/files/visual_arts_unit_specific_plan_2-14.pdf | Art department faculty, students, staff
Visual Arts | Visual Arts Safety Training (initial) | Initial | Initial Visual Arts Safety training is required for all personnel working in an Art studio | End of calendar year in which course ends or separation of employment + 30 years | EHS - Visual Arts Safety Initial Training - UP | Art department faculty, students, staff
Visual Arts | Visual Arts Safety Training (refresher) | Annual - August | Annual refresher training is required for all personnel working in an Art studio. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Visual Arts Safety Refresher Training - All Locations | Art department faculty, students, staff
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Athletics
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (non-research) | Annual - May | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Bloodborne Pathogens Training | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in Januar- | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | N/A | Maintenance, Housing & Food Services, potentially other areas
Cranes, Hoists & Slings | Crane/Hoist annual inspection | Annual - May | Annual "periodic" inspection of crane by vendor | Life of equipment | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone | Costs vary by crane type and vendor
Cranes, Hoists & Slings | Crane/hoist monthly inspection | Monthly | Monthly "frequent" inspection of crane by vendor or designated employee | End of calendar year + 3 years | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Daily inspection | Daily | Visual inspection of crane/hoist/sling prior to each use | N/A | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Hands-on user evaluation | Initial | Hands-on evaluation required for Bridge Crane operators | Period of employment in the work unit | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Inventory | Initial, review and update as needed | A listing of all cranes and hoists | Until superseded | Section 8.1.1 of the Crain, Hoist Sling Program Document | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Sling Annual inspection | Annual - May | Annual inspection of sling by Competent Person | Life of equipment | http://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Environmental Emergency Plans | Review and update EHERP plan | Annual - September | Review and update EHERP as needed (due to personnel or facility changes) and at least annually | Superseded/ updated + 1 year | http://ehs.psu.edu/environmental-emergency-plans/overview | Maintenance, Housing & Food Service, Director of Business Services, Laboratories
Environmental Emergency Plans | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/environmental_hazards_emergency_response_plan_self_audit.docx | Maintenance, Housing & Food Service, and other areas that have a pan
Environmental Emergency Plans | Spill kits | Varies | Maintain and re-stock spill kits in elevator mechanical rooms, laboratories, machine shops, kitchens, storage tank locations, and other areas that require spill response kits. | N/A | http://ehs.psu.edu/environmental-emergency-plans/overview | Any | replacement costs
Environmental Emergency Plans | Spill response training for hazardous materials, oils, and/or storage tanks | Annual | Provide EHERP training to affected employees annually | End of calendar year in which course ends or separation of employment + 30 years |  | Maintenance, Labs, Housing & Food Service
Environmental Emergency Plans | Tier II reporting (SARA) | Due March 1st | Report of any chemical (including road salt and other ice melting products) that exceeds the Threshold Planning Quantity, generally 10,000 pounds or more | Superseded/ outdated + 1 year | https://www.lipatts.pa.gov/Account/Login.aspx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Annual - June | Visual inspection of aboveground storage tanks; this is more comprehensive than the monthly inspection. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/annual_aboveground_storage_tank_inspection_checklist_ehs-064_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Monthly | Visual inspection of aboveground storage tanks; there are two forms, one for fuel/oil storage tanks and one for chemical storage tanks. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_aboveground_storage_tank_inspection_checklist_ehs-062_rev_5-21.docx | Maintenance
https://ehs.psu.edu/sites/ehs/files/monthly_chemical_aboveground_storage_tank_inspection_checklist_ehs-063_rev_5-21.docx
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Every 72 hours | Visual inspection for aboveground storage tanks of 21,000 gallons or greater | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/routine_aboveground_storage_tank_inspection_checklist_ehs-065_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Containment water release inspection | Varies | Visual inspection of rainwater captured by a containment facility prior to release | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/containment_water_release_inspection_checklist_ehs-067_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Observation of tank filling procedures | Varies | Observe and document filling of above- or below-ground tanks | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/product_delivery_observation_form_ehs-068_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | PADEP Regulated Storage Tank Registration | Annual | Certain PA DEP Regulated storage tanks must have an inspection by a PA DEP certified inspection as directed on storage tank registration. | Until superseded |  | Maintenance
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hearing Conservation | Medical Surveillance - hearing tests | Annual | Annual hearing test for employees in Hearing Conservation Program | Records kept by Occupational Medicine | http://ehs.psu.edu/hearing-conservation/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Occ Med at UP; contracted providers at campuses.
Hearing Conservation | Training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Hearing Conservation | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Multiple EHS programs | Boating Safety Training | Initial | Boating safety training is required by PA Fish & Boat Commission | End of calendar year in which course ends or separation of employment + 30 years | https://www.boat-ed.com/pennsylvania/ | Academics/Research
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
OPP / Athletics | Building Code (PA) including bleacher safety | Every 3 years | Bleachers must be inspected by an external party at least once every 3 years per PA Dep't of Labor & Industry | Life of equipment | N/A | Athletics, Student Affairs | External inspector fee varies
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Pest Management | Integrated Pest Management plan review | Annually | If you have an Integrated Pest Management Plan, review it annually to ensure it is up to date and that program is being followed as provided by the plan. | Until superseded/ updated + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-integrated-pest-management | Maintenance, Housing and Food Services
Pesticides | Application records | Varies | Pesticide application records must be kept for the past 3 years. | Date of application + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Eyewash | Prior to use | For pesticides being mixed from concentrates, a flowing eyewash must be present in the area where the pesticide is mixed. If the pesticide label says eye protection is required, then the applicators must carry bottled eyewash with them.
Pesticides | Eyewash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Inventory | Annual - January | Annual pesticide inventory (in CHIMs) | Date of acquisition + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | License | Annual | Copies of the annual Certified Applicator License and the Pesticide Business License must be up-to-date and available. | Until superseded | N/A | Maintenance, Labs/farms/research using pesticides
Pesticides | Pesticide storage area inspection | Monthly | Inspect pesticide storage area | End of calendar year + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Housing & Food Service, Labs/farms/research using pesticides
Pesticides | Worker Protection Standard Training | Annual | All employees who are not certified applicators and who work in areas where pesticides are used for agricultural applications, including greenhouses, must take annual training. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs/farms/research using pesticides
Powered Industrial Trucks (forklifts) | PIT annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone | External inspector fee varies
Powered Industrial Trucks (forklifts) | PIT daily inspection | Daily | Documented by operator | End of calendar year + 1 year | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT hands-on user evaluation | Every 3 years | Hands-on evaluation required for PIT (forklift) operators | Period of employment in the work unit | https://ehs.psu.edu/pit/forms | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT inventory | Initial, review and update as needed | Each work unit is responsible for keeping a list of all PITs within the work unit. | Until superseded |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT repair records | As needed | Retain all repair records | Life of equipment |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT user training | Initial | Initial classroom & hands-on training for users of PITs (forklifts) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Powered Industrial Truck (Forklift) Training | Maintenance, could be anyone
Process Safety Management (PSM) | Contractor Qualification Assessment | Annual | Pre-Qualification Data Reviewed by EHS | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors bidding on projects relating to PSM Covered Process Equipment
Process Safety Management (PSM) | Hazardous Line Opening Permit Training | Initial | Personnel who open PSM Covered Process equipment (e.g., pipes, vessels, tanks, etc.) must be trained on the Hazardous Line Opening Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Hazardous Line Opening Requirements | As needed | A Hazardous Line Opening Permit must be completed by PSM Authorized Employees when opening any PSM Covered equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | PSM Awareness & Contractor Responsibilities Training | Annual | Annual PSM Awareness and Contractor Responsibilities | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors working in or around Covered Process Areas
Process Safety Management (PSM) | PSM Steering Committee - Review | Annual | At least annually review the progress (e.g., metrics, incidents, etc.) and performance of PSM program | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, College of Ag, Athletics, Animal Resource Program, Risk Management
Process Safety Management (PSM) | Safe Work Permit Requirements | As needed | A Safe Work Permit must be completed for non-routine maintenance activities associated with PSM Covered Process Equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Safe Work Permit Training | Initial | Personnel who perform maintenance activities on PSM Covered Process Equipment must be trained on the Safe Work Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Radiation | Inventory Update | Annual - February | Annual inventory update | Date of acquisition + 1 year | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Regulated Medical Waste | Regulated Medical Waste Pickup (Campuses) | Quarterly or more often as needed | Regulated medical waste cannot remain on campus more than 90 days. Details on handling are in policy SY29. | End of calendar year + 2 years | http://ehs.psu.edu/infectious-waste-management/overview | Laboratories, Nurses
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Theater Rigging | Theater Rigging Inspection (annual) | Annual - January | Documented inspection by a Competent Inspector is required annually | Life of equipment | https://ehs.psu.edu/theatre-rigging/forms | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (Third Party) | Every 3 years | Documented inspection by a third party (outside vendor) is required every 3 years. | Life of equipment | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (visual) | Prior to Use | Rigging must be visually inspected before each use | N/A | https://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspector training | Initial | Training is required for Competent inspectors of theatrical rigging. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Repair Records | As needed | Retain all repair records | Life of equipment |  | Maintenance, Theater Department faculty/staff
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Bio Labs
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Asbestos | Asbestos assessment in equipment (e.g. fume hood liners, ovens, lab bench tops, etc.) | Before maintenance, repair or disposal | Contact EHS before maintenance, repair or disposal; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Biosafety | Autoclave quality control | Weekly | Verify effectiveness of sterilization with a biological indicator (Bacillus/Geobacillus spore vials, etc.), and use an indicator such as color-changing autoclave tape with each load to verify adequate sterilization. | N/A | N/A | Labs | ~$250/pack of 25 for spores
Biosafety | Biosafety cabinet annual inspection by third party | Annual | Inspection of biosafety cabinets for proper function must be performed annually by a third party. | Life of equipment | https://ehs.psu.edu/biosafety/biosafety-resources | Labs | Costs vary
Biosafety | Biosafety training | Initial | Training for personnel working with BSL-2 or higher organisms. | Records retained by CITI | https://citi.psu.edu | Labs
Biosafety/Office for Research Protections | Registration and review of Research and Teaching involving Biohazardous and Regulated Materials | Initially and every 3 years | Research and teaching activities involving biohazardous or regulated materials (including "Select Agents") must be reviewed and approved by the Institutional Biosafety Committee (IBC) prior to starting work. Resubmission required every 3 years. See policy RP11 (formerly SY24). | Until superseded (IBC maintains records) | https://www.research.psu.edu/ibc | Labs
Biosafety/Office for Research Protections | Vertebrate animal care and use (IACUC) | Initially and every 3 years | All work with vertebrate animals must be approved by IACUC. | IACUC maintains records | https://www.research.psu.edu/iacuc | Labs
Biosafety/Office for Research Protections | Vertebrate animal care and use (IACUC) training | Initial | Training is required for all employees involved in research with vertebrate animals. | IACUC maintains records | https://citi.psu.edu/ | Labs
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (research) | Annual - August | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | https://citi.psu.edu/ | Researchers working with bloodborne pathogens
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Facility Anti-Terrorism Standards | CFATS Inventory | Upon receipt | Upon receipt, update CHIMS database as required by SY39 | Upon receipt of the chemical + 2 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Facility Anti-Terrorism Standards | CFATS Top-Screen Forms | Within 60 Days of Possession | Chemicals of Interest above threshold quantity - must submit Top-Screen Form within 60 days | End of calendar year + 6 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or Waste Management Logbook (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | https://apps.opp.psu.edu/ehs_training/course_list.cfm?page_action=ViewClasses&course=378 | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | N/A | Maintenance, Housing & Food Services, potentially other areas
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Energized Electrical/ NFPA 70E annual evaluation | Annual - July | Annual evaluation of all employees authorized to perform electrical work (includes LOTO evaluation) | Period of employment in the work unit | https://ehs.psu.edu/energized-electrical-safety/forms | Engineering, Science labs, Arts | employee time
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Excavation Safety (OPP) | Excavation Safety PA 1-Call | Prior to work | A PA 1 Call shall be completed prior to any excavation/earth disturbance | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety Training | Annual - March | Competent person excavation training for anyone who performs excavation activities | End of calendar year in which course ends or separation of employement, + 30 years | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety trench inspection | Daily | A competent person shall complete a trench inspection daily, after a rainstorm, or if there is a hazardous condition | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hazardous Materials Shipping | Hazardous Materials/Dangerous Goods Shipping Training | Every 2 Years | Individuals who ship hazardous materials (biological, chemical, radioactive, and/or waste) and sign paperwork must receive DOT/IATA and/or NRC training every other year. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Maintenance, Janitorial, Housing & Food Service, Police Services
Hazmat shipping: Import/Export permits (Ethics & Compliance) | HazMat Shipments - Import/Export Permits (TSCA) | Prior to shipping internationally | Refer to Ethics & Compliance website and the EHS Hazardous Materials shipping program for information on importing or exporting hazardous materials | EHS retains forms | https://universityethics.psu.edu/export-compliance | Any
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring, exposure monitoring, and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene / Chemical Hygiene / Lab Safety / Biosafety | Commissioning of fume hoods and biosafety cabinets | Initial | Commissioning of fume hoods by 3rd party (test reports) prior to first performance test and use | Archive/Storage by Project Team; Biosafety Cabinets additionally by User | OPP Design and Construction Standards- D&C Standards (23.00.10.12) Lab Vent Systems | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre | Costs vary by hood type and vendor
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Industrial Hygiene / Laboratory Safety / Chemical Hygiene | Annual fume hood testing | Annual - as scheduled | Transitioned to OPP | Archived by EHS, historically, transitioned to OPP for U/Park |  | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety / Chemical Hygiene | Carcinogen hazard assessment and substance-specific control plans, as applicable, where determined necessary by initial exposure assessment | Initial and update annually | Wherever determined necessary by exposure level, or where required by OSHA regulation, substance-specific control plans shall be prepared. Use of carcinogens (including but not limited to materials regulated by individual OSHA substance-specific standards (e.g. formaldehyde, beryllium, arsenic, hexavalent chromium, cadmium, benzene, etc.) and similar highly hazardous materials must undergo a hazard assessment prior to work commencing. Engineering controls shall be used whenever possible. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/forms | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety/ Chemical Hygiene | Gas monitoring & alarms | As needed | Where gas monitors are installed or needed, follow procedures outlined in the Gas Monitoring Program. | See program | https://ehs.psu.edu/sites/ehs/files/gas_monitoring_program_-_final.docx | Labs, Engineering, Maintenance | Monitoring devices
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Develop & update Standard Operating Procedures (SOPs) | Initial | Develop SOPs for hazardous substances, equipment, and processes. Review annually as part of the USP review and update as necessary | Life of equipment | http://ehs.psu.edu/sops | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory & Research Safety Plan / Unit Specific Plan preparation and review | Initial, review and update as needed | Prepare a Unit Specific safety plan for each laboratory, and update annually | Until superseded/ updated + 1 year | http://ehs.psu.edu/sites/ehs/files/unit_specific_plan_form_template_added_ghs.doc | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory closeout (not moving anywhere) consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for closing a lab down permanently. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_closeout_certification.docx | Academics/Research
Laboratory Safety | Laboratory move to another institution - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab externally (outside PSU. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_external_move_guidelines.docx | Academics/Research
Laboratory Safety | Laboratory move within Penn State - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab internally (to other PSU space). | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_internal_move_guidelines.docx | Academics/Research
Laboratory Safety | Preserved specimens - hazard assessment | Prior to moving, handling, or disposal | Refer to the Laboratory Safety and Research Plan (line item 177) - content provided at LRSP Section 9.4. | N/A |  | Academics/Research, Museums
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety | Self-inspection | Annual - January | Laboratory self-inspection | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/lab_self_inspection_2022_-_form.docx | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (initial) | Initial | All laboratory personnel must complete initial Laboratory Safety training prior to working in the lab | End of calendar year in which course ends or separation of employment + 30 years | EHS - Initial Laboratory & Research Safety Training - University Park | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (refresher) | Annual - August | All laboratory personnel must complete Laboratory Safety refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS – Laboratory and Research Safety Refresher Training - All Locations | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Laboratory Safety/Office of Research Protections | Controlled substances - DEA registration | Initial | All researchers working with controlled substances must work with ORP to obtain and maintain their DEA registration | NA | https://www.research.psu.edu/controlsubs | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety; OPP | Pressure vessel inspection | Annual | Annual inspection of pressure vessels (autoclaves, boilers, etc.) by Labor & Industry. Managed by Risk Management through FM Global. | Keep current version | N/A | OPP, Maintenance, Laboratories
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | http://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Multiple EHS programs | Boating Safety Training | Initial | Boating safety training is required by PA Fish & Boat Commission | End of calendar year in which course ends or separation of employment + 30 years | https://www.boat-ed.com/pennsylvania/ | Academics/Research
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Clinical Human Research (IRB) protocol review | Prior to starting research project | IRB determines that clinical research protocols involving human subjects may require individual approval by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/qualitymanagement | Labs/research
Office for Research Protections | Diving Safety (research) certification | Initial | Scientific divers must be trained/certified | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety (research) dive log | After each dive | Scientific divers must submit a log of each dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety Plan review (research) | Prior to dive | Diving Safety Plan must be approved prior to each scientific dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Human Subjects Research (IRB) plan review | Prior to starting research project | All research involving human subjects must be approved by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/irb | Labs/research
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age | N/A | http://ehs.psu.edu/ppe/overview | All except office
Pest Management | Integrated Pest Management plan review | Annually | If you have an Integrated Pest Management Plan, review it annually to ensure it is up to date and that program is being followed as provided by the plan. | Until superseded/ updated + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-integrated-pest-management | Maintenance, Housing and Food Services
Pesticides | Application records | Varies | Pesticide application records must be kept for the past 3 years. | Date of application + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Eyewash | Prior to use | For pesticides being mixed from concentrates, a flowing eyewash must be present in the area where the pesticide is mixed. If the pesticide label says eye protection is required, then the applicators must carry bottled eyewash with them.
Pesticides | Eyewash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Inventory | Annual - January | Annual pesticide inventory (in CHIMs) | Date of acquisition + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | License | Annual | Copies of the annual Certified Applicator License and the Pesticide Business License must be up-to-date and available. | Until superseded | N/A | Maintenance, Labs/farms/research using pesticides
Pesticides | Pesticide storage area inspection | Monthly | Inspect pesticide storage area | End of calendar year + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Housing & Food Service, Labs/farms/research using pesticides
Pesticides | Worker Protection Standard Training | Annual | All employees who are not certified applicators and who work in areas where pesticides are used for agricultural applications, including greenhouses, must take annual training. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs/farms/research using pesticides
Radiation | Inventory Update | Annual - February | Annual inventory update | Date of acquisition + 1 year | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive material safety training | Annual | All users of radioactive materials must complete Initial training prior to using material, and refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS-Radionuclide Safety Education | Labs using Radioactive Materials
Radiation | Radioactive Material Survey | Daily | Survey after each use of radioactive material, decontaminate as needed | End of calendar year + 3 years | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive materials Lab Survey | Quarterly or Monthly | EHS conducts quarterly or monthly contamination survey of radiation-using labs | Records retained by EHS. Where representing exposure, maintain 30 years, or until license termination, whichever is longer. | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Regulated Medical Waste | Regulated Medical Waste Pickup (Campuses) | Quarterly or more often as needed | Regulated medical waste cannot remain on campus more than 90 days. Details on handling are in policy SY29. | End of calendar year + 2 years | http://ehs.psu.edu/infectious-waste-management/overview | Laboratories, Nurses
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Chem Labs
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Asbestos | Asbestos assessment in equipment (e.g. fume hood liners, ovens, lab bench tops, etc.) | Before maintenance, repair or disposal | Contact EHS before maintenance, repair or disposal; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Biosafety | Autoclave quality control | Weekly | Verify effectiveness of sterilization with a biological indicator (Bacillus/Geobacillus spore vials, etc.), and use an indicator such as color-changing autoclave tape with each load to verify adequate sterilization. | N/A | N/A | Labs | ~$250/pack of 25 for spores
Biosafety | Biosafety cabinet annual inspection by third party | Annual | Inspection of biosafety cabinets for proper function must be performed annually by a third party. | Life of equipment | https://ehs.psu.edu/biosafety/biosafety-resources | Labs | Costs vary
Biosafety/Office for Research Protections | Registration and review of Research and Teaching involving Biohazardous and Regulated Materials | Initially and every 3 years | Research and teaching activities involving biohazardous or regulated materials (including "Select Agents") must be reviewed and approved by the Institutional Biosafety Committee (IBC) prior to starting work. Resubmission required every 3 years. See policy RP11 (formerly SY24). | Until superseded (IBC maintains records) | https://www.research.psu.edu/ibc | Labs
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Bloodborne Pathogen | Bloodborne Pathogen training (research) | Annual - August | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | https://citi.psu.edu/ | Researchers working with bloodborne pathogens
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Facility Anti-Terrorism Standards | CFATS Inventory | Upon receipt | Upon receipt, update CHIMS database as required by SY39 | Upon receipt of the chemical + 2 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Facility Anti-Terrorism Standards | CFATS Top-Screen Forms | Within 60 Days of Possession | Chemicals of Interest above threshold quantity - must submit Top-Screen Form within 60 days | End of calendar year + 6 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or Waste Management Logbook (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | https://apps.opp.psu.edu/ehs_training/course_list.cfm?page_action=ViewClasses&course=378 | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | N/A | Maintenance, Housing & Food Services, potentially other areas
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Environmental / Regulatory Compliance Checklist | Environmental / Regulatory Compliance Checklist Review | Design phase of renovation / construction projects | Project Leaders and Professionals are to complete this form in eBuilder during design phase of OPP projects | N/A |  | OPP
Environmental Emergency Plans | Oil interceptors & oil/water separators inspection | Semiannually | Inspect oil interceptors and/or oil/water separators at least semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing drums (> 55 gallons) inspection | Monthly | Visual inspection of oil containing drums | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_drum_inspection_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing transformers (> 55 gallons) inspection | Semiannually | Visual inspection of transformer for leaks | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/transformer_inspection_checklist_rev_5-17.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Other oil-filled equipment (> 55 gallons) inspection | Varies | Visual inspection for leaks (see EHERP requirements) | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service, Labs
Environmental Emergency Plan / Storage Tanks | PADEP Regulated Storage Tank inspection by PADEP | Varies | Certain PA DEP regulated storage tanks must have an inspection a PA DEP certified inspection as directed on storage tank registration | Life of equipment | http://www.dep.pa.gov/Business/Land/Tanks/Pages/Forms-and-Applications.aspx | Maintenance
Environmental Emergency Plans | Review and update EHERP plan | Annual - September | Review and update EHERP as needed (due to personnel or facility changes) and at least annually | Superseded/ updated + 1 year | http://ehs.psu.edu/environmental-emergency-plans/overview | Maintenance, Housing & Food Service, Director of Business Services, Laboratories
Environmental Emergency Plans | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/environmental_hazards_emergency_response_plan_self_audit.docx | Maintenance, Housing & Food Service, and other areas that have a pan
Environmental Emergency Plans | Spill kits | Varies | Maintain and re-stock spill kits in elevator mechanical rooms, laboratories, machine shops, kitchens, storage tank locations, and other areas that require spill response kits. | N/A | http://ehs.psu.edu/environmental-emergency-plans/overview | Any | replacement costs
Environmental Emergency Plans | Spill response training for hazardous materials, oils, and/or storage tanks | Annual | Provide EHERP training to affected employees annually | End of calendar year in which course ends or separation of employment + 30 years |  | Maintenance, Labs, Housing & Food Service
Environmental Emergency Plans | Tier II reporting (SARA) | Due March 1st | Report of any chemical (including road salt and other ice melting products) that exceeds the Threshold Planning Quantity, generally 10,000 pounds or more | Superseded/ outdated + 1 year | https://www.lipatts.pa.gov/Account/Login.aspx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Annual - June | Visual inspection of aboveground storage tanks; this is more comprehensive than the monthly inspection. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/annual_aboveground_storage_tank_inspection_checklist_ehs-064_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Monthly | Visual inspection of aboveground storage tanks; there are two forms, one for fuel/oil storage tanks and one for chemical storage tanks. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_aboveground_storage_tank_inspection_checklist_ehs-062_rev_5-21.docx | Maintenance
https://ehs.psu.edu/sites/ehs/files/monthly_chemical_aboveground_storage_tank_inspection_checklist_ehs-063_rev_5-21.docx
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Every 72 hours | Visual inspection for aboveground storage tanks of 21,000 gallons or greater | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/routine_aboveground_storage_tank_inspection_checklist_ehs-065_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Containment water release inspection | Varies | Visual inspection of rainwater captured by a containment facility prior to release | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/containment_water_release_inspection_checklist_ehs-067_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Observation of tank filling procedures | Varies | Observe and document filling of above- or below-ground tanks | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/product_delivery_observation_form_ehs-068_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | PADEP Regulated Storage Tank Registration | Annual | Certain PA DEP Regulated storage tanks must have an inspection by a PA DEP certified inspection as directed on storage tank registration. | Until superseded |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground storage tank annual inspection | Annual - June | Check of underground storage tank monitoring equipment by vendor | Life of equipment |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank facility inspection | Monthly | Underground tank facility general inspection | Varies by tank size |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank sump inspections | Monthly | Underground storage sump inspections where no monitor is present must be inspected monthly | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_underground_storage_tank_sunp_inspection_checklist_ehs-070_rev_5-21.docx | Maintenance
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Excavation Safety (OPP) | Excavation Safety PA 1-Call | Prior to work | A PA 1 Call shall be completed prior to any excavation/earth disturbance | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety Training | Annual - March | Competent person excavation training for anyone who performs excavation activities | End of calendar year in which course ends or separation of employement, + 30 years | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety trench inspection | Daily | A competent person shall complete a trench inspection daily, after a rainstorm, or if there is a hazardous condition | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Explosive Management Program | Explosive Permit | Annual | State Permit to purchase explosive materials | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Explosive Management Program | Inventory Count | Annual | Annual physical inventory count of explosive materials | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Explosive Management Program | License Renewal | Every 3 years | Federal license application through ATF | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Explosive Management Program | Magazine Permit | Annual | State license to store explosive materials | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hazardous Materials Shipping | Hazardous Materials/Dangerous Goods Shipping Training | Every 2 Years | Individuals who ship hazardous materials (biological, chemical, radioactive, and/or waste) and sign paperwork must receive DOT/IATA and/or NRC training every other year. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Maintenance, Janitorial, Housing & Food Service, Police Services
Hazmat shipping: Import/Export permits (Ethics & Compliance) | HazMat Shipments - Import/Export Permits (TSCA) | Prior to shipping internationally | Refer to Ethics & Compliance website and the EHS Hazardous Materials shipping program for information on importing or exporting hazardous materials | EHS retains forms | https://universityethics.psu.edu/export-compliance | Any
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring, exposure monitoring, and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene / Chemical Hygiene / Lab Safety / Biosafety | Commissioning of fume hoods and biosafety cabinets | Initial | Commissioning of fume hoods by 3rd party (test reports) prior to first performance test and use | Archive/Storage by Project Team; Biosafety Cabinets additionally by User | OPP Design and Construction Standards- D&C Standards (23.00.10.12) Lab Vent Systems | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre | Costs vary by hood type and vendor
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Industrial Hygiene / Laboratory Safety / Chemical Hygiene | Annual fume hood testing | Annual - as scheduled | Transitioned to OPP | Archived by EHS, historically, transitioned to OPP for U/Park |  | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety / Chemical Hygiene / | Carcinogen hazard assessment and substance-specific control plans, as applicable, where determined necessary by initial exposure assessment | Initial and update annually | Wherever determined necessary by exposure level, or where required by OSHA regulation, substance-specific control plans shall be prepared. Use of carcinogens (including but not limited to materials regulated by individual OSHA substance-specific standards (e.g. formaldehyde, beryllium, arsenic, hexavalent chromium, cadmium, benzene, etc.) and similar highly hazardous materials must undergo a hazard assessment prior to work commencing. Engineering controls shall be used whenever possible. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/forms | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety/ Chemical Hygiene | Gas monitoring & alarms | As needed | Where gas monitors are installed or needed, follow procedures outlined in the Gas Monitoring Program. | See program | https://ehs.psu.edu/sites/ehs/files/gas_monitoring_program_-_final.docx | Labs, Engineering, Maintenance | Monitoring devices
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Develop & update Standard Operating Procedures (SOPs) | Initial | Develop SOPs for hazardous substances, equipment, and processes. Review annually as part of the USP review and update as necessary | Life of equipment | http://ehs.psu.edu/sops | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory & Research Safety Plan / Unit Specific Plan preparation and review | Initial, review and update as needed | Prepare a Unit Specific safety plan for each laboratory, and update annually | Until superseded/ updated + 1 year | http://ehs.psu.edu/sites/ehs/files/unit_specific_plan_form_template_added_ghs.doc | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory closeout (not moving anywhere) consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for closing a lab down permanently. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_closeout_certification.docx | Academics/Research
Laboratory Safety | Laboratory move to another institution - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab externally (outside PSU. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_external_move_guidelines.docx | Academics/Research
Laboratory Safety | Laboratory move within Penn State - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab internally (to other PSU space). | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_internal_move_guidelines.docx | Academics/Research
Laboratory Safety | Preserved specimens - hazard assessment | Prior to moving, handling, or disposal | Refer to the Laboratory Safety and Research Plan (line item 177) - content provided at LRSP Section 9.4. | N/A |  | Academics/Research, Museums
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety | Self-inspection | Annual - January | Laboratory self-inspection | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/lab_self_inspection_2022_-_form.docx | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (initial) | Initial | All laboratory personnel must complete initial Laboratory Safety training prior to working in the lab | End of calendar year in which course ends or separation of employment + 30 years | EHS - Initial Laboratory & Research Safety Training - University Park | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (refresher) | Annual - August | All laboratory personnel must complete Laboratory Safety refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS – Laboratory and Research Safety Refresher Training - All Locations | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Laboratory Safety/Office of Research Protections | Controlled substances - DEA registration | Initial | All researchers working with controlled substances must work with ORP to obtain and maintain their DEA registration | NA | https://www.research.psu.edu/controlsubs | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety; OPP | Pressure vessel inspection | Annual | Annual inspection of pressure vessels (autoclaves, boilers, etc.) by Labor & Industry. Managed by Risk Management through FM Global. | Keep current version | N/A | OPP, Maintenance, Laboratories
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Lockout/Tagout | LOTO Affected Personnel Training | Initial | Initial training for employees who do not perform LOTO but may be affected by equipment that is LOTO'd | End of calendar year in which course ends or separation of employment + 30 years | EHS - Lockout/Tagout Affected Employee Training | Maintenance, could be anyone
Lockout/Tagout | LOTO contractor notification forms | Prior to contractor beginning work | Work units must exchange LOTO procedures with contractors servicing/maintaining PSU equipment that requires LOTO. This form documents that information exchange. | End of calendar year + 1 year | https://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Lockout/Tagout | LOTO evaluation | Annual - July | Annual evaluation of all employees authorized to use Lockout/Tagout procedures | Period of employment in the work unit | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO lock removal form | As needed | Documentation of lock removal by anyone other than designated employee to whom lock is assigned | End of calendar year + 1 year |  | Maintenance, could be anyone
Lockout/Tagout | LOTO procedures | Initial and update as needed | Documented LOTO procedure is required for equipment with multiple energy sources | Life of equipment | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO training | Initial | Initial training for employees who perform Lockout/Tagout | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | http://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Multiple EHS programs | Boating Safety Training | Initial | Boating safety training is required by PA Fish & Boat Commission | End of calendar year in which course ends or separation of employment + 30 years | https://www.boat-ed.com/pennsylvania/ | Academics/Research
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Clinical Human Research (IRB) protocol review | Prior to starting research project | IRB determines that clinical research protocols involving human subjects may require individual approval by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/qualitymanagement | Labs/research
Office for Research Protections | Diving Safety (research) certification | Initial | Scientific divers must be trained/certified | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety (research) dive log | After each dive | Scientific divers must submit a log of each dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety Plan review (research) | Prior to dive | Diving Safety Plan must be approved prior to each scientific dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Human Subjects Research (IRB) plan review | Prior to starting research project | All research involving human subjects must be approved by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/irb | Labs/research
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Pesticides | Application records | Varies | Pesticide application records must be kept for the past 3 years. | Date of application + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Eyewash | Prior to use | For pesticides being mixed from concentrates, a flowing eyewash must be present in the area where the pesticide is mixed. If the pesticide label says eye protection is required, then the applicators must carry bottled eyewash with them.
Pesticides | Eyewash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Inventory | Annual - January | Annual pesticide inventory (in CHIMs) | Date of acquisition + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | License | Annual | Copies of the annual Certified Applicator License and the Pesticide Business License must be up-to-date and available. | Until superseded | N/A | Maintenance, Labs/farms/research using pesticides
Pesticides | Pesticide storage area inspection | Monthly | Inspect pesticide storage area | End of calendar year + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/pesticide_facility_annual_self_audit_0.docx | Maintenance, Housing & Food Service, Labs/farms/research using pesticides
Pesticides | Worker Protection Standard Training | Annual | All employees who are not certified applicators and who work in areas where pesticides are used for agricultural applications, including greenhouses, must take annual training. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs/farms/research using pesticides
Powered Industrial Trucks (forklifts) | PIT user training | Initial | Initial classroom & hands-on training for users of PITs (forklifts) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Powered Industrial Truck (Forklift) Training | Maintenance, could be anyone
Process Safety Management (PSM) | Contractor Qualification Assessment | Annual | Pre-Qualification Data Reviewed by EHS | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors bidding on projects relating to PSM Covered Process Equipment
Process Safety Management (PSM) | Hazardous Line Opening Permit Training | Initial | Personnel who open PSM Covered Process equipment (e.g., pipes, vessels, tanks, etc.) must be trained on the Hazardous Line Opening Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Hazardous Line Opening Requirements | As needed | A Hazardous Line Opening Permit must be completed by PSM Authorized Employees when opening any PSM Covered equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | PSM Awareness & Contractor Responsibilities Training | Annual | Annual PSM Awareness and Contractor Responsibilities | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors working in or around Covered Process Areas
Process Safety Management (PSM) | PSM Steering Committee - Review | Annual | At least annually review the progress (e.g., metrics, incidents, etc.) and performance of PSM program | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, College of Ag, Athletics, Animal Resource Program, Risk Management
Process Safety Management (PSM) | Safe Work Permit Requirements | As needed | A Safe Work Permit must be completed for non-routine maintenance activities associated with PSM Covered Process Equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Safe Work Permit Training | Initial | Personnel who perform maintenance activities on PSM Covered Process Equipment must be trained on the Safe Work Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Radiation | Inventory Update | Annual - February | Annual inventory update | Date of acquisition + 1 year | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive material safety training | Annual | All users of radioactive materials must complete Initial training prior to using material, and refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS-Radionuclide Safety Education | Labs using Radioactive Materials
Radiation | Radioactive Material Survey | Daily | Survey after each use of radioactive material, decontaminate as needed | End of calendar year + 3 years | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive materials Lab Survey | Quarterly or Monthly | EHS conducts quarterly or monthly contamination survey of radiation-using labs | Records retained by EHS. Where representing exposure, maintain 30 years, or until license termination, whichever is longer. | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Regulated Medical Waste | Regulated Medical Waste Pickup (Campuses) | Quarterly or more often as needed | Regulated medical waste cannot remain on campus more than 90 days. Details on handling are in policy SY29. | End of calendar year + 2 years | http://ehs.psu.edu/infectious-waste-management/overview | Laboratories, Nurses
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## ITS
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Asbestos | Asbestos assessment prior to any maintenance, renovation or demolition | Before maintenance, renovation or demolition. | Contact EHS before conducting any work in / on pre-1990 buildings. Exterior renovations such as roofing do not have a date cut-off; contact EHS before any exterior work. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Asbestos | Asbestos awareness training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
Confined Space | Confined Space Awareness training | Initial | Training recommended for employees who may work around Confined Spaces but will not be entering those spaces. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Permit | Prior to entry | Permit must be filled out and approved, and hazards must be identified and mitigated, prior to entering confined space | End of calendar year + 1 year | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Training | Initial | Training required for any employee who will be entering a Permit-Required Confined Space | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space inventory | Initial, and updated as needed | Keep an up-to-date list of confined spaces on each campus | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space labeling | Initial | Label all Permit-Required Confined Spaces | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | cost depends on sign type (~$10-150)
Confined Space | Confined Space Rescue | Prior to entry | Prior to entering a Permit-Required Confined Space, a Confined Space Rescue Team must be available and on-call (in-house or county EMS or provider) | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | CS rescue equipment costs at UP
Confined Space | Confined Space Rescue Training | Annual - June | In-house Confined Space Rescue Teams must be trained/refreshed at least once every 12 months | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Inform Contractors | Prior to entry | Inform contractors of confined spaces and any known hazards relevant to their scope of work and remind them that they must comply with OSHA Confined Space standards | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E annual evaluation | Annual - July | Annual evaluation of all employees authorized to perform electrical work (includes LOTO evaluation) | Period of employment in the work unit | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E contractor/host employer meeting | As needed | Document the Contractor / Host Employer meeting. | Superseded/ updated + 1 year |  | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E equipment/task-specific work plans | Initial, review and update as needed | Documentation containing information pertaining to each electrical task and its corresponding PPE requirements shall be maintained by the work unit. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E PPE & equipment inspections | Varies | Electrical safety equipment such as insulating gloves, covers, arc flash suits require inspection. See Appendix G of program for complete list of equipment and frequency | Life of equipment | http://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, could be anyone | Glove inspection ~$40 per pair, every 6 months.
Electrical Safety | Energized Electrical/ NFPA 70E Self-Review of devices | Annual - July | Self-review of electrical devices in laboratories for safety compliance, specifically for machinery >50V. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Engineering, Science labs, Arts | employee time
Electrical Safety | Energized Electrical/ NFPA 70E Training | Every 3 years | Initial classroom training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Energized Electrical/NFPA 70E Arc Flash Training | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E work permit | As needed | Copies of all energized electrical work permits (appendix A) must be provided to both the work unit Safety Officer and the EHS Department upon completion of the task. | End of calendar year + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring, exposure monitoring, and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lockout/Tagout | LOTO Affected Personnel Training | Initial | Initial training for employees who do not perform LOTO but may be affected by equipment that is LOTO'd | End of calendar year in which course ends or separation of employment + 30 years | EHS - Lockout/Tagout Affected Employee Training | Maintenance, could be anyone
Lockout/Tagout | LOTO contractor notification forms | Prior to contractor beginning work | Work units must exchange LOTO procedures with contractors servicing/maintaining PSU equipment that requires LOTO. This form documents that information exchange. | End of calendar year + 1 year | https://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Lockout/Tagout | LOTO evaluation | Annual - July | Annual evaluation of all employees authorized to use Lockout/Tagout procedures | Period of employment in the work unit | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO lock removal form | As needed | Documentation of lock removal by anyone other than designated employee to whom lock is assigned | End of calendar year + 1 year |  | Maintenance, could be anyone
Lockout/Tagout | LOTO procedures | Initial and update as needed | Documented LOTO procedure is required for equipment with multiple energy sources | Life of equipment | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO training | Initial | Initial training for employees who perform Lockout/Tagout | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Theater Rigging | Theater Rigging Inspection (annual) | Annual - January | Documented inspection by a Competent Inspector is required annually | Life of equipment | https://ehs.psu.edu/theatre-rigging/forms | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (Third Party) | Every 3 years | Documented inspection by a third party (outside vendor) is required every 3 years. | Life of equipment | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (visual) | Prior to Use | Rigging must be visually inspected before each use | N/A | https://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspector training | Initial | Training is required for Competent inspectors of theatrical rigging. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Repair Records | As needed | Retain all repair records | Life of equipment |  | Maintenance, Theater Department faculty/staff
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Classroom and Office
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Clinical Human Research (IRB) protocol review | Prior to starting research project | IRB determines that clinical research protocols involving human subjects may require individual approval by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/qualitymanagement | Labs/research
Office for Research Protections | Human Subjects Research (IRB) plan review | Prior to starting research project | All research involving human subjects must be approved by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/irb | Labs/research
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Engineering Labs
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Asbestos | Asbestos assessment in equipment (e.g. fume hood liners, ovens, lab bench tops, etc.) | Before maintenance, repair or disposal | Contact EHS before maintenance, repair or disposal; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Facility Anti-Terrorism Standards | CFATS Inventory | Upon receipt | Upon receipt, update CHIMS database as required by SY39 | Upon receipt of the chemical + 2 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Facility Anti-Terrorism Standards | CFATS Top-Screen Forms | Within 60 Days of Possession | Chemicals of Interest above threshold quantity - must submit Top-Screen Form within 60 days | End of calendar year + 6 years | http://ehs.psu.edu/chemical-inventory-management/overview | Labs
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or Waste Management Logbook (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | N/A | Maintenance, Housing & Food Services, potentially other areas
Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
Confined Space | Confined Space Awareness training | Initial | Training recommended for employees who may work around Confined Spaces but will not be entering those spaces. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Permit | Prior to entry | Permit must be filled out and approved, and hazards must be identified and mitigated, prior to entering confined space | End of calendar year + 1 year | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Training | Initial | Training required for any employee who will be entering a Permit-Required Confined Space | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space inventory | Initial, and updated as needed | Keep an up-to-date list of confined spaces on each campus | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space labeling | Initial | Label all Permit-Required Confined Spaces | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | cost depends on sign type (~$10-150)
Confined Space | Confined Space Rescue | Prior to entry | Prior to entering a Permit-Required Confined Space, a Confined Space Rescue Team must be available and on-call (in-house or county EMS or provider) | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | CS rescue equipment costs at UP
Confined Space | Confined Space Rescue Training | Annual - June | In-house Confined Space Rescue Teams must be trained/refreshed at least once every 12 months | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Inform Contractors | Prior to entry | Inform contractors of confined spaces and any known hazards relevant to their scope of work and remind them that they must comply with OSHA Confined Space standards | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Cranes, Hoists & Slings | Crane/Hoist annual inspection | Annual - May | Annual "periodic" inspection of crane by vendor | Life of equipment | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone | Costs vary by crane type and vendor
Cranes, Hoists & Slings | Crane/hoist monthly inspection | Monthly | Monthly "frequent" inspection of crane by vendor or designated employee | End of calendar year + 3 years | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Daily inspection | Daily | Visual inspection of crane/hoist/sling prior to each use | N/A | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Hands-on user evaluation | Initial | Hands-on evaluation required for Bridge Crane operators | Period of employment in the work unit | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Inventory | Initial, review and update as needed | A listing of all cranes and hoists | Until superseded | Section 8.1.1 of the Crain, Hoist Sling Program Document | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Sling Annual inspection | Annual - May | Annual inspection of sling by Competent Person | Life of equipment | http://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E annual evaluation | Annual - July | Annual evaluation of all employees authorized to perform electrical work (includes LOTO evaluation) | Period of employment in the work unit | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E contractor/host employer meeting | As needed | Document the Contractor / Host Employer meeting. | Superseded/ updated + 1 year |  | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E equipment/task-specific work plans | Initial, review and update as needed | Documentation containing information pertaining to each electrical task and its corresponding PPE requirements shall be maintained by the work unit. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E PPE & equipment inspections | Varies | Electrical safety equipment such as insulating gloves, covers, arc flash suits require inspection. See Appendix G of program for complete list of equipment and frequency | Life of equipment | http://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, could be anyone | Glove inspection ~$40 per pair, every 6 months.
Electrical Safety | Energized Electrical/ NFPA 70E Self-Review of devices | Annual - July | Self-review of electrical devices in laboratories for safety compliance, specifically for machinery >50V. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Engineering, Science labs, Arts | employee time
Electrical Safety | Energized Electrical/ NFPA 70E Training | Every 3 years | Initial classroom training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Energized Electrical/NFPA 70E Arc Flash Training | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E work permit | As needed | Copies of all energized electrical work permits (appendix A) must be provided to both the work unit Safety Officer and the EHS Department upon completion of the task. | End of calendar year + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Environmental / Regulatory Compliance Checklist | Environmental / Regulatory Compliance Checklist Review | Design phase of renovation / construction projects | Project Leaders and Professionals are to complete this form in eBuilder during design phase of OPP projects | N/A |  | OPP
Environmental Emergency Plan / Storage Tanks | PADEP Regulated Storage Tank inspection by PADEP | Varies | Certain PA DEP regulated storage tanks must have an inspection a PA DEP certified inspection as directed on storage tank registration | Life of equipment | http://www.dep.pa.gov/Business/Land/Tanks/Pages/Forms-and-Applications.aspx | Maintenance
Environmental Emergency Plans | Oil interceptors & oil/water separators inspection | Semiannually | Inspect oil interceptors and/or oil/water separators at least semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing drums (> 55 gallons) inspection | Monthly | Visual inspection of oil containing drums | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_drum_inspection_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing transformers (> 55 gallons) inspection | Semiannually | Visual inspection of transformer for leaks | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/transformer_inspection_checklist_rev_5-17.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Other oil-filled equipment (> 55 gallons) inspection | Varies | Visual inspection for leaks (see EHERP requirements) | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service, Labs
Environmental Emergency Plans | Review and update EHERP plan | Annual - September | Review and update EHERP as needed (due to personnel or facility changes) and at least annually | Superseded/ updated + 1 year | http://ehs.psu.edu/environmental-emergency-plans/overview | Maintenance, Housing & Food Service, Director of Business Services, Laboratories
Environmental Emergency Plans | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/environmental_hazards_emergency_response_plan_self_audit.docx | Maintenance, Housing & Food Service, and other areas that have a pan
Environmental Emergency Plans | Spill kits | Varies | Maintain and re-stock spill kits in elevator mechanical rooms, laboratories, machine shops, kitchens, storage tank locations, and other areas that require spill response kits. | N/A | http://ehs.psu.edu/environmental-emergency-plans/overview | Any | replacement costs
Environmental Emergency Plans | Spill response training for hazardous materials, oils, and/or storage tanks | Annual | Provide EHERP training to affected employees annually | End of calendar year in which course ends or separation of employment + 30 years |  | Maintenance, Labs, Housing & Food Service
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Annual - June | Visual inspection of aboveground storage tanks; this is more comprehensive than the monthly inspection. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/annual_aboveground_storage_tank_inspection_checklist_ehs-064_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Monthly | Visual inspection of aboveground storage tanks; there are two forms, one for fuel/oil storage tanks and one for chemical storage tanks. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_aboveground_storage_tank_inspection_checklist_ehs-062_rev_5-21.docx | Maintenance
https://ehs.psu.edu/sites/ehs/files/monthly_chemical_aboveground_storage_tank_inspection_checklist_ehs-063_rev_5-21.docx
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Every 72 hours | Visual inspection for aboveground storage tanks of 21,000 gallons or greater | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/routine_aboveground_storage_tank_inspection_checklist_ehs-065_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Containment water release inspection | Varies | Visual inspection of rainwater captured by a containment facility prior to release | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/containment_water_release_inspection_checklist_ehs-067_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Observation of tank filling procedures | Varies | Observe and document filling of above- or below-ground tanks | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/product_delivery_observation_form_ehs-068_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | PADEP Regulated Storage Tank Registration | Annual | Certain PA DEP Regulated storage tanks must have an inspection by a PA DEP certified inspection as directed on storage tank registration. | Until superseded |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground storage tank annual inspection | Annual - June | Check of underground storage tank monitoring equipment by vendor | Life of equipment |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank facility inspection | Monthly | Underground tank facility general inspection | Varies by tank size |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank sump inspections | Monthly | Underground storage sump inspections where no monitor is present must be inspected monthly | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_underground_storage_tank_sunp_inspection_checklist_ehs-070_rev_5-21.docx | Maintenance
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Excavation Safety (OPP) | Excavation Safety PA 1-Call | Prior to work | A PA 1 Call shall be completed prior to any excavation/earth disturbance | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety Training | Annual - March | Competent person excavation training for anyone who performs excavation activities | End of calendar year in which course ends or separation of employement, + 30 years | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety trench inspection | Daily | A competent person shall complete a trench inspection daily, after a rainstorm, or if there is a hazardous condition | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Explosive Management Program | Explosive Permit | Annual | State Permit to purchase explosive materials | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Explosive Management Program | Inventory Count | Annual | Annual physical inventory count of explosive materials | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Explosive Management Program | License Renewal | Every 3 years | Federal license application through ATF | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Explosive Management Program | Magazine Permit | Annual | State license to store explosive materials | Expiration of permit + 3 years | http://ehs.psu.edu/explosive-materials-management/overview | Research using explosive materials
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hazardous Materials Shipping | Hazardous Materials/Dangerous Goods Shipping Training | Every 2 Years | Individuals who ship hazardous materials (biological, chemical, radioactive, and/or waste) and sign paperwork must receive DOT/IATA and/or NRC training every other year. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Maintenance, Janitorial, Housing & Food Service, Police Services
Hazmat shipping: Import/Export permits (Ethics & Compliance) | HazMat Shipments - Import/Export Permits (TSCA) | Prior to shipping internationally | Refer to Ethics & Compliance website and the EHS Hazardous Materials shipping program for information on importing or exporting hazardous materials | EHS retains forms | https://universityethics.psu.edu/export-compliance | Any
Hearing Conservation | Medical Surveillance - hearing tests | Annual | Annual hearing test for employees in Hearing Conservation Program | Records kept by Occupational Medicine | http://ehs.psu.edu/hearing-conservation/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Occ Med at UP; contracted providers at campuses.
Hearing Conservation | Training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Hearing Conservation | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring, exposure monitoring, and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene / Chemical Hygiene / Lab Safety / Biosafety | Commissioning of fume hoods and biosafety cabinets | Initial | Commissioning of fume hoods by 3rd party (test reports) prior to first performance test and use | Archive/Storage by Project Team; Biosafety Cabinets additionally by User | OPP Design and Construction Standards- D&C Standards (23.00.10.12) Lab Vent Systems | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre | Costs vary by hood type and vendor
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Industrial Hygiene / Laboratory Safety / Chemical Hygiene | Annual fume hood testing | Annual - as scheduled | Transitioned to OPP | Archived by EHS, historically, transitioned to OPP for U/Park |  | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety / Chemical Hygiene | Carcinogen hazard assessment and substance-specific control plans, as applicable, where determined necessary by initial exposure assessment | Initial and update annually | Wherever determined necessary by exposure level, or where required by OSHA regulation, substance-specific control plans shall be prepared. Use of carcinogens (including but not limited to materials regulated by individual OSHA substance-specific standards (e.g. formaldehyde, beryllium, arsenic, hexavalent chromium, cadmium, benzene, etc.) and similar highly hazardous materials must undergo a hazard assessment prior to work commencing. Engineering controls shall be used whenever possible. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/forms | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety/ Chemical Hygiene | Gas monitoring & alarms | As needed | Where gas monitors are installed or needed, follow procedures outlined in the Gas Monitoring Program. | See program | https://ehs.psu.edu/sites/ehs/files/gas_monitoring_program_-_final.docx | Labs, Engineering, Maintenance | Monitoring devices
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Develop & update Standard Operating Procedures (SOPs) | Initial | Develop SOPs for hazardous substances, equipment, and processes. Review annually as part of the USP review and update as necessary | Life of equipment | http://ehs.psu.edu/sops | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory & Research Safety Plan / Unit Specific Plan preparation and review | Initial, review and update as needed | Prepare a Unit Specific safety plan for each laboratory, and update annually | Until superseded/ updated + 1 year | http://ehs.psu.edu/sites/ehs/files/unit_specific_plan_form_template_added_ghs.doc | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Laboratory closeout (not moving anywhere) consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for closing a lab down permanently. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_closeout_certification.docx | Academics/Research
Laboratory Safety | Laboratory move to another institution - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab externally (outside PSU. | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_external_move_guidelines.docx | Academics/Research
Laboratory Safety | Laboratory move within Penn State - consultation & inspection | Begin ~2 months prior to closing out lab space | Consult with EHS and complete relevant documented inspection for moving a lab internally (to other PSU space). | EHS retains forms | https://ehs.psu.edu/sites/ehs/files/laboratory_internal_move_guidelines.docx | Academics/Research
Laboratory Safety | Preserved specimens - hazard assessment | Prior to moving, handling, or disposal | Refer to the Laboratory Safety and Research Plan (line item 177) - content provided at LRSP Section 9.4. | N/A |  | Academics/Research, Museums
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety | Self-inspection | Annual - January | Laboratory self-inspection | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/lab_self_inspection_2022_-_form.docx | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (initial) | Initial | All laboratory personnel must complete initial Laboratory Safety training prior to working in the lab | End of calendar year in which course ends or separation of employment + 30 years | EHS - Initial Laboratory & Research Safety Training - University Park | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety | Training (refresher) | Annual - August | All laboratory personnel must complete Laboratory Safety refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS – Laboratory and Research Safety Refresher Training - All Locations | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Laboratory Safety/Office of Research Protections | Controlled substances - DEA registration | Initial | All researchers working with controlled substances must work with ORP to obtain and maintain their DEA registration | NA | https://www.research.psu.edu/controlsubs | Laboratories (Science, Engineering, Agriculture, etc.)
Laboratory Safety; OPP | Pressure vessel inspection | Annual | Annual inspection of pressure vessels (autoclaves, boilers, etc.) by Labor & Industry. Managed by Risk Management through FM Global. | Keep current version | N/A | OPP, Maintenance, Laboratories
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Lockout/Tagout | LOTO Affected Personnel Training | Initial | Initial training for employees who do not perform LOTO but may be affected by equipment that is LOTO'd | End of calendar year in which course ends or separation of employment + 30 years | EHS - Lockout/Tagout Affected Employee Training | Maintenance, could be anyone
Lockout/Tagout | LOTO contractor notification forms | Prior to contractor beginning work | Work units must exchange LOTO procedures with contractors servicing/maintaining PSU equipment that requires LOTO. This form documents that information exchange. | End of calendar year + 1 year | https://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Lockout/Tagout | LOTO evaluation | Annual - July | Annual evaluation of all employees authorized to use Lockout/Tagout procedures | Period of employment in the work unit | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO lock removal form | As needed | Documentation of lock removal by anyone other than designated employee to whom lock is assigned | End of calendar year + 1 year |  | Maintenance, could be anyone
Lockout/Tagout | LOTO procedures | Initial and update as needed | Documented LOTO procedure is required for equipment with multiple energy sources | Life of equipment | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO training | Initial | Initial training for employees who perform Lockout/Tagout | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | http://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Multiple EHS programs | Boating Safety Training | Initial | Boating safety training is required by PA Fish & Boat Commission | End of calendar year in which course ends or separation of employment + 30 years | https://www.boat-ed.com/pennsylvania/ | Academics/Research
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Clinical Human Research (IRB) protocol review | Prior to starting research project | IRB determines that clinical research protocols involving human subjects may require individual approval by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/qualitymanagement | Labs/research
Office for Research Protections | Diving Safety (research) certification | Initial | Scientific divers must be trained/certified | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety (research) dive log | After each dive | Scientific divers must submit a log of each dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Diving Safety Plan review (research) | Prior to dive | Diving Safety Plan must be approved prior to each scientific dive | Maintained by ORP | https://www.research.psu.edu/scidive | Labs/research
Office for Research Protections | Human Subjects Research (IRB) plan review | Prior to starting research project | All research involving human subjects must be approved by the Institutional Review Board (IRB) | Maintained by ORP | https://www.research.psu.edu/irb | Labs/research
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Powered Industrial Trucks (forklifts) | PIT annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone | External inspector fee varies
Powered Industrial Trucks (forklifts) | PIT daily inspection | Daily | Documented by operator | End of calendar year + 1 year | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT hands-on user evaluation | Every 3 years | Hands-on evaluation required for PIT (forklift) operators | Period of employment in the work unit | https://ehs.psu.edu/pit/forms | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT inventory | Initial, review and update as needed | Each work unit is responsible for keeping a list of all PITs within the work unit. | Until superseded |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT repair records | As needed | Retain all repair records | Life of equipment |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT user training | Initial | Initial classroom & hands-on training for users of PITs (forklifts) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Powered Industrial Truck (Forklift) Training | Maintenance, could be anyone
Process Safety Management (PSM) | Contractor Qualification Assessment | Annual | Pre-Qualification Data Reviewed by EHS | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors bidding on projects relating to PSM Covered Process Equipment
Process Safety Management (PSM) | Hazardous Line Opening Permit Training | Initial | Personnel who open PSM Covered Process equipment (e.g., pipes, vessels, tanks, etc.) must be trained on the Hazardous Line Opening Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Hazardous Line Opening Requirements | As needed | A Hazardous Line Opening Permit must be completed by PSM Authorized Employees when opening any PSM Covered equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | PSM Awareness & Contractor Responsibilities Training | Annual | Annual PSM Awareness and Contractor Responsibilities | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors working in or around Covered Process Areas
Process Safety Management (PSM) | PSM Steering Committee - Review | Annual | At least annually review the progress (e.g., metrics, incidents, etc.) and performance of PSM program | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, College of Ag, Athletics, Animal Resource Program, Risk Management
Process Safety Management (PSM) | Safe Work Permit Requirements | As needed | A Safe Work Permit must be completed for non-routine maintenance activities associated with PSM Covered Process Equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Safe Work Permit Training | Initial | Personnel who perform maintenance activities on PSM Covered Process Equipment must be trained on the Safe Work Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Radiation | Inventory Update | Annual - February | Annual inventory update | Date of acquisition + 1 year | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive material safety training | Annual | All users of radioactive materials must complete Initial training prior to using material, and refresher training annually | End of calendar year in which course ends or separation of employment + 30 years | EHS-Radionuclide Safety Education | Labs using Radioactive Materials
Radiation | Radioactive Material Survey | Daily | Survey after each use of radioactive material, decontaminate as needed | End of calendar year + 3 years | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radioactive materials Lab Survey | Quarterly or Monthly | EHS conducts quarterly or monthly contamination survey of radiation-using labs | Records retained by EHS. Where representing exposure, maintain 30 years, or until license termination, whichever is longer. | https://ehs.psu.edu/radioactive-materials/radioactive-materials-requirements-guidelines | Labs using Radioactive Materials
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Refrigerant | Annual self-audit for appliance owners | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self-audit_for_appliance_owners.docx | Maintenance, Housing & Foods
Refrigerant | Annual self-audit for service providers | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self_audit_for_service_providers.docx | Maintenance, Housing & Foods
Refrigerant | Appliance Inventory | Annual - January | Inventory of all refrigeration units containing 50 or more pounds of circuit | Until superseded | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Certification | Initial | Maintain certification(s) for employees who use refrigerants | Period of employment in the work unit + 3 years | N/A | Maintenance, Housing & Foods
Refrigerant | Leak Rate Calculations | Varies | For all appliances containing 50 pounds or more of refrigerant, leak rates must be calculated each time refrigerant is added. There is a spreadsheet which performs these calculations. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Refrigerant Inventory | As needed | Keep a log of all refrigerant usage from purchase to return for reclamation | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Service records | Varies | Maintain required service records and submit them to the appliance owner, including all records referring to refrigerant used, removed, or reclaimed. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Regulated Medical Waste | Regulated Medical Waste Pickup (Campuses) | Quarterly or more often as needed | Regulated medical waste cannot remain on campus more than 90 days. Details on handling are in policy SY29. | End of calendar year + 2 years | http://ehs.psu.edu/infectious-waste-management/overview | Laboratories, Nurses
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## OPP
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Asbestos | Asbestos assessment in equipment (e.g. fume hood liners, ovens, lab bench tops, etc.) | Before maintenance, repair or disposal | Contact EHS before maintenance, repair or disposal; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Asbestos | Asbestos assessment prior to any maintenance, renovation or demolition | Before maintenance, renovation or demolition. | Contact EHS before conducting any work in / on pre-1990 buildings. Exterior renovations such as roofing do not have a date cut-off; contact EHS before any exterior work. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Asbestos | Asbestos awareness training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality
Asbestos - Structural Demolition | Asbestos assessment prior to demolition or removal of structural members within a building | Before demolition or removal of structural members | Contact EHS before demolition or removal of structural members; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Possible sampling and testing fees, depending scope and funding source.
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (non-research) | Annual - May | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Bloodborne Pathogens Training | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | N/A | Maintenance, Housing & Food Services, potentially other areas
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
Confined Space | Confined Space Awareness training | Initial | Training recommended for employees who may work around Confined Spaces but will not be entering those spaces. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Permit | Prior to entry | Permit must be filled out and approved, and hazards must be identified and mitigated, prior to entering confined space | End of calendar year + 1 year | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Training | Initial | Training required for any employee who will be entering a Permit-Required Confined Space | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space inventory | Initial, and updated as needed | Keep an up-to-date list of confined spaces on each campus | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space labeling | Initial | Label all Permit-Required Confined Spaces | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | cost depends on sign type (~$10-150)
Confined Space | Confined Space Rescue | Prior to entry | Prior to entering a Permit-Required Confined Space, a Confined Space Rescue Team must be available and on-call (in-house or county EMS or provider) | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | CS rescue equipment costs at UP
Confined Space | Confined Space Rescue Training | Annual - June | In-house Confined Space Rescue Teams must be trained/refreshed at least once every 12 months | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Inform Contractors | Prior to entry | Inform contractors of confined spaces and any known hazards relevant to their scope of work and remind them that they must comply with OSHA Confined Space standards | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Contractor Safety (OPP) | Contractor safety (construction and non-construction) |  | See OPP contractor/construction safety requirements in Design & Construction standards Division 00. Note: This currently applies only to contractors hired by OPP. | N/A | https://wikispaces.psu.edu/download/attachments/357076600/PSU%20OPP%20Contractor_Safety_Requirements.pdf?version=2&modificationDate=1550257929000&api=v2 | Maintenance, Housing & Food Services, Information Technology
Cranes, Hoists & Slings | Crane/Hoist annual inspection | Annual - May | Annual "periodic" inspection of crane by vendor | Life of equipment | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone | Costs vary by crane type and vendor
Cranes, Hoists & Slings | Crane/hoist monthly inspection | Monthly | Monthly "frequent" inspection of crane by vendor or designated employee | End of calendar year + 3 years | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Daily inspection | Daily | Visual inspection of crane/hoist/sling prior to each use | N/A | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Hands-on user evaluation | Initial | Hands-on evaluation required for Bridge Crane operators | Period of employment in the work unit | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Inventory | Initial, review and update as needed | A listing of all cranes and hoists | Until superseded | Section 8.1.1 of the Crain, Hoist Sling Program Document | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Sling Annual inspection | Annual - May | Annual inspection of sling by Competent Person | Life of equipment | http://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E annual evaluation | Annual - July | Annual evaluation of all employees authorized to perform electrical work (includes LOTO evaluation) | Period of employment in the work unit | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E contractor/host employer meeting | As needed | Document the Contractor / Host Employer meeting. | Superseded/ updated + 1 year |  | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E equipment/task-specific work plans | Initial, review and update as needed | Documentation containing information pertaining to each electrical task and its corresponding PPE requirements shall be maintained by the work unit. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E PPE & equipment inspections | Varies | Electrical safety equipment such as insulating gloves, covers, arc flash suits require inspection. See Appendix G of program for complete list of equipment and frequency | Life of equipment | http://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, could be anyone | Glove inspection ~$40 per pair, every 6 months.
Electrical Safety | Energized Electrical/ NFPA 70E Self-Review of devices | Annual - July | Self-review of electrical devices in laboratories for safety compliance, specifically for machinery >50V. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Engineering, Science labs, Arts | employee time
Electrical Safety | Energized Electrical/ NFPA 70E Training | Every 3 years | Initial classroom training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Energized Electrical/NFPA 70E Arc Flash Training | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E work permit | As needed | Copies of all energized electrical work permits (appendix A) must be provided to both the work unit Safety Officer and the EHS Department upon completion of the task. | End of calendar year + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Environmental / Regulatory Compliance Checklist | Environmental / Regulatory Compliance Checklist Review | Design phase of renovation / construction projects | Project Leaders and Professionals are to complete this form in eBuilder during design phase of OPP projects | N/A |  | OPP
Environmental Emergency Plans | Grease trap clean-out documentation | Varies | Removal of grease from grease traps must be documented. | End of calendar year + 3 years | N/A | Maintenance, Housing & Food Service
Environmental Emergency Plans | Hydraulic elevators (> 55 gallons) inspection | Quarterly | Visual inspection of hydraulic system for leaks | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/elevator_inspection_report.doc | Maintenance, Housing & Food Service | UP: Performed by OPP. Campuses: vendor performs
Environmental Emergency Plans | Oil interceptors & oil/water separators inspection | Semiannually | Inspect oil interceptors and/or oil/water separators at least semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing drums (> 55 gallons) inspection | Monthly | Visual inspection of oil containing drums | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_drum_inspection_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing transformers (> 55 gallons) inspection | Semiannually | Visual inspection of transformer for leaks | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/transformer_inspection_checklist_rev_5-17.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Other oil-filled equipment (> 55 gallons) inspection | Varies | Visual inspection for leaks (see EHERP requirements) | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service, Labs
Environmental Emergency Plan / Storage Tanks | PADEP Regulated Storage Tank inspection by PADEP | Varies | Certain PA DEP regulated storage tanks must have an inspection a PA DEP certified inspection as directed on storage tank registration | Life of equipment | http://www.dep.pa.gov/Business/Land/Tanks/Pages/Forms-and-Applications.aspx | Maintenance
Environmental Emergency Plans | Review and update EHERP plan | Annual - September | Review and update EHERP as needed (due to personnel or facility changes) and at least annually | Superseded/ updated + 1 year | http://ehs.psu.edu/environmental-emergency-plans/overview | Maintenance, Housing & Food Service, Director of Business Services, Laboratories
Environmental Emergency Plans | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/environmental_hazards_emergency_response_plan_self_audit.docx | Maintenance, Housing & Food Service, and other areas that have a pan
Environmental Emergency Plans | Spill kits | Varies | Maintain and re-stock spill kits in elevator mechanical rooms, laboratories, machine shops, kitchens, storage tank locations, and other areas that require spill response kits. | N/A | http://ehs.psu.edu/environmental-emergency-plans/overview | Any | replacement costs
Environmental Emergency Plans | Spill response training for hazardous materials, oils, and/or storage tanks | Annual | Provide EHERP training to affected employees annually | End of calendar year in which course ends or separation of employment + 30 years |  | Maintenance, Labs, Housing & Food Service
Environmental Emergency Plans | Tier II reporting (SARA) | Due March 1st | Report of any chemical (including road salt and other ice melting products) that exceeds the Threshold Planning Quantity, generally 10,000 pounds or more | Superseded/ outdated + 1 year | https://www.lipatts.pa.gov/Account/Login.aspx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Annual - June | Visual inspection of aboveground storage tanks; this is more comprehensive than the monthly inspection. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/annual_aboveground_storage_tank_inspection_checklist_ehs-064_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Monthly | Visual inspection of aboveground storage tanks; there are two forms, one for fuel/oil storage tanks and one for chemical storage tanks. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_aboveground_storage_tank_inspection_checklist_ehs-062_rev_5-21.docx | Maintenance
https://ehs.psu.edu/sites/ehs/files/monthly_chemical_aboveground_storage_tank_inspection_checklist_ehs-063_rev_5-21.docx
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Every 72 hours | Visual inspection for aboveground storage tanks of 21,000 gallons or greater | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/routine_aboveground_storage_tank_inspection_checklist_ehs-065_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Containment water release inspection | Varies | Visual inspection of rainwater captured by a containment facility prior to release | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/containment_water_release_inspection_checklist_ehs-067_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Observation of tank filling procedures | Varies | Observe and document filling of above- or below-ground tanks | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/product_delivery_observation_form_ehs-068_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | PADEP Regulated Storage Tank Registration | Annual | Certain PA DEP Regulated storage tanks must have an inspection by a PA DEP certified inspection as directed on storage tank registration. | Until superseded |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground storage tank annual inspection | Annual - June | Check of underground storage tank monitoring equipment by vendor | Life of equipment |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank facility inspection | Monthly | Underground tank facility general inspection | Varies by tank size |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank sump inspections | Monthly | Underground storage sump inspections where no monitor is present must be inspected monthly | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_underground_storage_tank_sunp_inspection_checklist_ehs-070_rev_5-21.docx | Maintenance
Environmental real estate assessment | Environmental due diligence | Prior to leasing / purchasing real estate | If pondering leasing/purchasing/accepting non-PSU real estate, follow Finance and Business Real Estate process. | N/A |  | OPP, campus leadership
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Excavation Safety (OPP) | Excavation Safety PA 1-Call | Prior to work | A PA 1 Call shall be completed prior to any excavation/earth disturbance | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety Training | Annual - March | Competent person excavation training for anyone who performs excavation activities | End of calendar year in which course ends or separation of employement, + 30 years | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety trench inspection | Daily | A competent person shall complete a trench inspection daily, after a rainstorm, or if there is a hazardous condition | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection | Automatic Fire Suppression Systems | Varies | All Testing / Inspection / Maintenance in accordance with appropriate NFPA standard / FM Global Recommendations for specific system (Sprinkler / Gaseous Agent / Standpipe / Fire Pumps / Backflow Devices etc.) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention and Protection; OPP | Fire Protection Systems: Report Impairments | Onset and end of impairment | When fire safety systems (alarms, sprinklers, etc.) are impaired (such as due to electrical or water failure, or for repairs), report to FM Global and use the Red Tag system as appropriate. | Duration of impairment | https://www.fmglobal.com/products-and-services/education-and-training/client-learning-solutions/~/media/64C97CB2A7004C18BA3A938A610FF429.ashx | Maintenance, H&FS
Fire Prevention/Protection | Automatic Sprinkler System inspection | Monthly | Inspect locked control valves with electronic tamper switches monthly; record pressure readings; investigate if change of 10% or more. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System inspection | Weekly | Inspect locked control valves without electronic tamper switches weekly | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System main drain flow test | Annual | Test main drain flow annually (per NFPA 25) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System tamper switch test | Semiannually | Test Supervisory/Tamper switches semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System water flow alarm test | Quarterly | Test water flow alarms quarterly (per NFPA 25); | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Building Fire Department Connection inspection | Quarterly | Inspect building fire department connections to ensure clear access and operation | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Building Fire Protection Pumps | Weekly or Monthly | Start pump - no flow running (Churn) weekly for Diesel driven, monthly for electric pumps (per NFPA 25) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Building Fire Protection Pumps | Annual | Annual pump inspection and flow test (per NFPA 25) - full flow/performance test and inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Curb box valve inspection & test | Annual - October | Inspect cover for accessibility; fully close and then fully open valve | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Dry sprinkler/fire suppression systems | Annual - October | Check and maintain low point drains annually prior to freezing weather, and as needed to ensure all water is drained from system piping. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems dry pipe trip test | Annual - October | Conduct partial trip test annually | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems full flow trip test | Every 3 Years | Conduct full flow trip test | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems inspection | Weekly / Monthly | Inspect valves, ensure locks; inspect gauges and record pressures (weekly without tamper switch, monthly with tamper switch) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems test | Quarterly | Test water flow alarms quarterly (per NFPA 25); test priming water; test low air alarm | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Emergency generator test | Weekly | Start and verify proper operation | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention/Protection | Emergency lighting / illuminated exit signs | Varies | Monthly activation test to ensure automatic lighting operation; Annual power test | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire Alarm System inspection & test | Annual - October | Inspect, maintain, and test fire alarm systems in accordance with NFPA 72 Standard "National Fire Alarm and Signaling Code" by qualified individual (manual pull stations, heat/smoke detectors, back-up batteries, etc.) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire curtain - inspect / test / maintain | Varies | Maintain fire curtain in accordance with NFPA Standard 80. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Theater
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire Hydrant testing | Annual | Flushing/testing of fire hydrant by water authority or campus staff | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Monthly | Monthly cleaning is required for cooking operations using solid-fuel-burning cooking appliances | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Quarterly | Quarterly cleaning is required for high-volume or high-smoke/grease cooking operations such as 24-hour cooking, charbroiling, or Wok cooking. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Semiannually - June & December | Cleaning of kitchen cooking exhaust devices (hoods, grease-removal devices, fans, ducts, etc.) at least semi-annually if grease accumulation is observed | Until superseded | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Fire Suppression System Inspection | Semiannually - June & December | Semi-annual inspection, maintenance and testing of fixed fire protection system (per NFPA 17A) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services | Costs vary
Fire Prevention/Protection | Fire safety - Vital Building Information | Annually | Pesticide storage buildings, if they catch fire, should not be extinguished with water as runoff would be toxic. Smoke can also be toxic. EHERP should include this information, and building should have appropriate signage. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Agriculture
Fire Prevention/Protection | Fire suppression system backflow protection | Annual | Conduct full-flow test in excess of the greatest sprinkler demand | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service | Vendor charge
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
Fire Prevention/Protection | Smoke control system - Inspection / testing / maintenance | Varies | Ensure systems are maintained in operable condition and perform as designed. System performance testing/inspection/maintenance in accordance with appropriate National Fire Protection Association (NFPA) standard for type system. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hazardous Materials Shipping | Hazardous Materials/Dangerous Goods Shipping Training | Every 2 Years | Individuals who ship hazardous materials (biological, chemical, radioactive, and/or waste) and sign paperwork must receive DOT/IATA and/or NRC training every other year. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Maintenance, Janitorial, Housing & Food Service, Police Services
Hazmat shipping: Import/Export permits (Ethics & Compliance) | HazMat Shipments - Import/Export Permits (TSCA) | Prior to shipping internationally | Refer to Ethics & Compliance website and the EHS Hazardous Materials shipping program for information on importing or exporting hazardous materials | EHS retains forms | https://universityethics.psu.edu/export-compliance | Any
Hearing Conservation | Medical Surveillance - hearing tests | Annual | Annual hearing test for employees in Hearing Conservation Program | Records kept by Occupational Medicine | http://ehs.psu.edu/hearing-conservation/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Occ Med at UP; contracted providers at campuses.
Hearing Conservation | Training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Hearing Conservation | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene / Chemical Hygiene / Lab Safety / Biosafety | Commissioning of fume hoods and biosafety cabinets | Initial | Commissioning of fume hoods by 3rd party (test reports) prior to first performance test and use | Archive/Storage by Project Team; Biosafety Cabinets additionally by User |  | Labs, Engineering. Maintenance | Costs vary by hood type and vendor
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Industrial Hygiene / Laboratory Safety / Chemical Hygiene | Annual fume hood testing | Annual - as scheduled | Transitioned to OPP | Archived by EHS, historically, transitioned to OPP for U/Park |  | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety / Chemical Hygiene | Carcinogen hazard assessment and substance-specific control plans, as applicable, where determined necessary by initial exposure assessment | Initial and update annually | Wherever determined necessary by exposure level, or where required by OSHA regulation, substance-specific control plans shall be prepared. Use of carcinogens (including but not limited to materials regulated by individual OSHA substance-specific standards (e.g. formaldehyde, beryllium, arsenic, hexavalent chromium, cadmium, benzene, etc.) and similar highly hazardous materials must undergo a hazard assessment prior to work commencing. Engineering controls shall be used whenever possible. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/forms | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety/ Chemical Hygiene | Gas monitoring & alarms | As needed | Where gas monitors are installed or needed, follow procedures outlined in the Gas Monitoring Program. | See program | https://ehs.psu.edu/sites/ehs/files/gas_monitoring_program_-_final.docx | Labs, Engineering, Maintenance | Monitoring devices
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Laboratory Safety; OPP | Pressure vessel inspection | Annual | Annual inspection of pressure vessels (autoclaves, boilers, etc.) by Labor & Industry. Managed by Risk Management through FM Global. | Keep current version | N/A | OPP, Maintenance, Laboratories
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead in building materials | Assessment of Lead in other building materials (flashing, window camings, etc.) | Prior to demolition / work that affects lead-containing material | Contact EHS prior to any work that could affect lead-containing materials. This includes but is not limited to: lead flashing, window camings, lead-lined walls for X-ray suites, etc. | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, Residence Hall Housekeeping, OPP PMs, PCs, Designers | sampling and testing fees vary
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Lead Paint | Assessment of lead paint in all maintenance, renovation or demolition that affects paint | Before maintenance, renovation or demolition that affects paint | Follow EHS / OPP Lead Paint Procedures | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP | Possible sampling and testing fees, depending scope and funding source.
Lead Paint | Assessment of lead paint in pre-1978 residential housing (non-undergraduate) and child-occupied facilities (e.g. daycare) | Before maintenance, renovation or demolition that affects paint | Contact EHS prior to any work that could affect paint. | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Lead Paint | Lead paint awareness training | Prior to initial exposure | Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality
Lockout/Tagout | LOTO Affected Personnel Training | Initial | Initial training for employees who do not perform LOTO but may be affected by equipment that is LOTO'd | End of calendar year in which course ends or separation of employment + 30 years | EHS - Lockout/Tagout Affected Employee Training | Maintenance, could be anyone
Lockout/Tagout | LOTO contractor notification forms | Prior to contractor beginning work | Work units must exchange LOTO procedures with contractors servicing/maintaining PSU equipment that requires LOTO. This form documents that information exchange. | End of calendar year + 1 year | https://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Lockout/Tagout | LOTO evaluation | Annual - July | Annual evaluation of all employees authorized to use Lockout/Tagout procedures | Period of employment in the work unit | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO lock removal form | As needed | Documentation of lock removal by anyone other than designated employee to whom lock is assigned | End of calendar year + 1 year |  | Maintenance, could be anyone
Lockout/Tagout | LOTO procedures | Initial and update as needed | Documented LOTO procedure is required for equipment with multiple energy sources | Life of equipment | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO training | Initial | Initial training for employees who perform Lockout/Tagout | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | http://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Mobile Crane Safety (OPP) | Crane Inspection | Prior to each use of equipment | Pre-use Inspection using the NCCCO Mobile Crane Inspection Form | End of calendar year + 4 years | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | Crane Inspection | Annual | Annual inspection of sling by 3rd Party | Life of equipment | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | Crane Operator Training | Every 5 Years | Written Exam and Hands-on evaluation required for Crane operators | End of calendar year in which course ends or separation of employment + 30 years | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | PA One Call prior to Crane setup | Prior to each set-up of equipment | Complete Pa One Call prior to crane set up | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | Rigger 1 Training | Every 5 Years | Written Exam and Hands-on evaluation required for Rigger 1 | End of calendar year in which course ends or separation of employment + 30 years | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Mobile Crane Safety (OPP) | Rigging Inspection | Prior to each use of equipment | Follow EHS/OPP Chain/Sling Inspection Program | End of calendar year + 4 years | https://opp.psu.edu/sites/opp/files/crane_safety_guidelines_0.pdf | Maintenance, Engineering, Agriculture, could be anyone
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
OPP / Athletics | Building Code (PA) including bleacher safety | Every 3 years | Bleachers must be inspected by an external party at least once every 3 years per PA Dep't of Labor & Industry | Life of equipment | N/A | Athletics, Student Affairs | External inspector fee varies
OPP / Construction fencing | Construction fencing (Temporary & Worksite Barricading) | Duration of construction | Maintain appropriate fencing/barricading of construction worksites as outlined in OPP Design & Construction standard 01 50 00. | N/A | https://wikispaces.psu.edu/display/OPPDCS/01+50+00+TEMPORARY+FACILITIES+AND+CONTROLS | Maintenance, H&FS
OPP / Industrial Hygiene | Paint spraying operations hazard assessment | Initial and update annually | Paint spraying operations shall undergo hazard assessment prior to work commencing. Spray booths or other engineering controls may be required. | End of calendar year + 1 year | N/A | OPP | employee time; potentially installation of ventilation hoods
PCB building materials | Assess for PCBs prior to all maintenance, renovation or demolition in / on pre-1980 facilities | Before maintenance, renovation or demolition. | Contact EHS before conducting maintenance, renovations or demolition in / on pre-1980 buildings. | Records retained by EHS | N/Ahttps://ehs.psu.edu/PCB-Containing%20Building%20Material%20Management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Pest Management | Integrated Pest Management plan review | Annually | If you have an Integrated Pest Management Plan, review it annually to ensure it is up to date and that program is being followed as provided by the plan. | Until superseded/ updated + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-integrated-pest-management | Maintenance, Housing and Food Services
Pesticides | Application records | Varies | Pesticide application records must be kept for the past 3 years. | Date of application + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Eyewash | Prior to use | For pesticides being mixed from concentrates, a flowing eyewash must be present in the area where the pesticide is mixed. If the pesticide label says eye protection is required, then the applicators must carry bottled eyewash with them.
Pesticides | Eyewash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Inventory | Annual - January | Annual pesticide inventory (in CHIMs) | Date of acquisition + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | License | Annual | Copies of the annual Certified Applicator License and the Pesticide Business License must be up-to-date and available. | Until superseded | N/A | Maintenance, Labs/farms/research using pesticides
Pesticides | Pesticide storage area inspection | Monthly | Inspect pesticide storage area | End of calendar year + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Housing & Food Service, Labs/farms/research using pesticides
Pesticides | Worker Protection Standard Training | Annual | All employees who are not certified applicators and who work in areas where pesticides are used for agricultural applications, including greenhouses, must take annual training. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs/farms/research using pesticides
Powered Industrial Trucks (forklifts) | PIT annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone | External inspector fee varies
Powered Industrial Trucks (forklifts) | PIT daily inspection | Daily | Documented by operator | End of calendar year + 1 year | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT hands-on user evaluation | Every 3 years | Hands-on evaluation required for PIT (forklift) operators | Period of employment in the work unit | https://ehs.psu.edu/pit/forms | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT inventory | Initial, review and update as needed | Each work unit is responsible for keeping a list of all PITs within the work unit. | Until superseded |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT repair records | As needed | Retain all repair records | Life of equipment |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT user training | Initial | Initial classroom & hands-on training for users of PITs (forklifts) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Powered Industrial Truck (Forklift) Training | Maintenance, could be anyone
Process Safety Management (PSM) | Contractor Qualification Assessment | Annual | Pre-Qualification Data Reviewed by EHS | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors bidding on projects relating to PSM Covered Process Equipment
Process Safety Management (PSM) | Hazardous Line Opening Permit Training | Initial | Personnel who open PSM Covered Process equipment (e.g., pipes, vessels, tanks, etc.) must be trained on the Hazardous Line Opening Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Hazardous Line Opening Requirements | As needed | A Hazardous Line Opening Permit must be completed by PSM Authorized Employees when opening any PSM Covered equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | PSM Awareness & Contractor Responsibilities Training | Annual | Annual PSM Awareness and Contractor Responsibilities | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | All Contractors working in or around Covered Process Areas
Process Safety Management (PSM) | PSM Steering Committee - Review | Annual | At least annually review the progress (e.g., metrics, incidents, etc.) and performance of PSM program | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, College of Ag, Athletics, Animal Resource Program, Risk Management
Process Safety Management (PSM) | Safe Work Permit Requirements | As needed | A Safe Work Permit must be completed for non-routine maintenance activities associated with PSM Covered Process Equipment | Records retained by EHS | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Process Safety Management (PSM) | Safe Work Permit Training | Initial | Personnel who perform maintenance activities on PSM Covered Process Equipment must be trained on the Safe Work Permit requirements | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/process-safety-management/requirements-guidelines | OPP, Work Unit Maintenance groups, etc.
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Refrigerant | Annual self-audit for appliance owners | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self-audit_for_appliance_owners.docx | Maintenance, Housing & Foods
Refrigerant | Annual self-audit for service providers | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self_audit_for_service_providers.docx | Maintenance, Housing & Foods
Refrigerant | Appliance Inventory | Annual - January | Inventory of all refrigeration units containing 50 or more pounds of circuit | Until superseded | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Certification | Initial | Maintain certification(s) for employees who use refrigerants | Period of employment in the work unit + 3 years | N/A | Maintenance, Housing & Foods
Refrigerant | Leak Rate Calculations | Varies | For all appliances containing 50 pounds or more of refrigerant, leak rates must be calculated each time refrigerant is added. There is a spreadsheet which performs these calculations. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Refrigerant Inventory | As needed | Keep a log of all refrigerant usage from purchase to return for reclamation | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Service records | Varies | Maintain required service records and submit them to the appliance owner, including all records referring to refrigerant used, removed, or reclaimed. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Regulated Medical Waste | Regulated Medical Waste Pickup (Campuses) | Quarterly or more often as needed | Regulated medical waste cannot remain on campus more than 90 days. Details on handling are in policy SY29. | End of calendar year + 2 years | http://ehs.psu.edu/infectious-waste-management/overview | Laboratories, Nurses
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Theater Rigging | Theater Rigging Inspection (annual) | Annual - January | Documented inspection by a Competent Inspector is required annually | Life of equipment | https://ehs.psu.edu/theatre-rigging/forms | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (Third Party) | Every 3 years | Documented inspection by a third party (outside vendor) is required every 3 years. | Life of equipment | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (visual) | Prior to Use | Rigging must be visually inspected before each use | N/A | https://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspector training | Initial | Training is required for Competent inspectors of theatrical rigging. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Repair Records | As needed | Retain all repair records | Life of equipment |  | Maintenance, Theater Department faculty/staff
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Events
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Emergency Evacuations & Fire Drills- Residence Halls | Monthly | Fire Drills are required in Residence Halls monthly when classes are in session | End of calendar year + 7 years | https://policy.psu.edu/policies/sy28 | Residence Life, Police Services, Housing
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Multiple EHS programs | Boating Safety Training | Initial | Boating safety training is required by PA Fish & Boat Commission | End of calendar year in which course ends or separation of employment + 30 years | https://www.boat-ed.com/pennsylvania/ | Academics/Research
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Powered Industrial Trucks (forklifts) | PIT annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone | External inspector fee varies
Powered Industrial Trucks (forklifts) | PIT daily inspection | Daily | Documented by operator | End of calendar year + 1 year | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT hands-on user evaluation | Every 3 years | Hands-on evaluation required for PIT (forklift) operators | Period of employment in the work unit | https://ehs.psu.edu/pit/forms | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT inventory | Initial, review and update as needed | Each work unit is responsible for keeping a list of all PITs within the work unit. | Until superseded |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT repair records | As needed | Retain all repair records | Life of equipment |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT user training | Initial | Initial classroom & hands-on training for users of PITs (forklifts) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Powered Industrial Truck (Forklift) Training | Maintenance, could be anyone
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Theater Rigging | Theater Rigging Inspection (annual) | Annual - January | Documented inspection by a Competent Inspector is required annually | Life of equipment | https://ehs.psu.edu/theatre-rigging/forms | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (Third Party) | Every 3 years | Documented inspection by a third party (outside vendor) is required every 3 years. | Life of equipment | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (visual) | Prior to Use | Rigging must be visually inspected before each use | N/A | https://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspector training | Initial | Training is required for Competent inspectors of theatrical rigging. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Repair Records | As needed | Retain all repair records | Life of equipment |  | Maintenance, Theater Department faculty/staff
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## H&FS
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs |  | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Asbestos | Asbestos assessment in equipment (e.g. fume hood liners, ovens, lab bench tops, etc.) | Before maintenance, repair or disposal | Contact EHS before maintenance, repair or disposal; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Asbestos | Asbestos assessment prior to any maintenance, renovation or demolition | Before maintenance, renovation or demolition. | Contact EHS before conducting any work in / on pre-1990 buildings. Exterior renovations such as roofing do not have a date cut-off; contact EHS before any exterior work. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Asbestos | Asbestos awareness training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality
Asbestos - Structural Demolition | Asbestos assessment prior to demolition or removal of structural members within a building | Before demolition or removal of structural members | Contact EHS before demolition or removal of structural members; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Possible sampling and testing fees, depending scope and funding source.
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (non-research) | Annual - May | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Bloodborne Pathogens Training | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Emergency Evacuations & Fire Drills- Residence Halls | Monthly | Fire Drills are required in Residence Halls monthly when classes are in session | End of calendar year + 7 years | https://policy.psu.edu/policies/sy28 | Residence Life, Police Services, Housing
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | N/A | Maintenance, Housing & Food Services, potentially other areas
Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
Confined Space | Confined Space Awareness training | Initial | Training required for employees who may work around Confined Spaces but will not be entering those spaces. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Permit | Prior to entry | Permit must be filled out and approved, and hazards must be identified and mitigated, prior to entering confined space | End of calendar year + 1 year | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Training | Initial | Training required for any employee who will be entering a Permit-Required Confined Space | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space inventory | Initial, and updated as needed | Keep an up-to-date list of confined spaces on each campus | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space labeling | Initial | Label all Permit-Required Confined Spaces | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | cost depends on sign type (~$10-150)
Confined Space | Confined Space Rescue | Prior to entry | Prior to entering a Permit-Required Confined Space, a Confined Space Rescue Team must be available and on-call (in-house or county EMS or provider) | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | CS rescue equipment costs at UP
Confined Space | Confined Space Rescue Training | Annual - June | In-house Confined Space Rescue Teams must be trained/refreshed at least once every 12 months | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Inform Contractors | Prior to entry | Inform contractors of confined spaces and any known hazards relevant to their scope of work and remind them that they must comply with OSHA Confined Space standards | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E annual evaluation | Annual - July | Annual evaluation of all employees authorized to perform electrical work (includes LOTO evaluation) | Period of employment in the work unit | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E contractor/host employer meeting | As needed | Document the Contractor / Host Employer meeting. | Superseded/ updated + 1 year |  | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E equipment/task-specific work plans | Initial, review and update as needed | Documentation containing information pertaining to each electrical task and its corresponding PPE requirements shall be maintained by the work unit. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E PPE & equipment inspections | Varies | Electrical safety equipment such as insulating gloves, covers, arc flash suits require inspection. See Appendix G of program for complete list of equipment and frequency | Life of equipment | http://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, could be anyone | Glove inspection ~$40 per pair, every 6 months.
Electrical Safety | Energized Electrical/ NFPA 70E Self-Review of devices | Annual - July | Self-review of electrical devices in laboratories for safety compliance, specifically for machinery >50V. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Engineering, Science labs, Arts | employee time
Electrical Safety | Energized Electrical/ NFPA 70E Training | Every 3 years | Initial classroom training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Energized Electrical/NFPA 70E Arc Flash Training | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E work permit | As needed | Copies of all energized electrical work permits (appendix A) must be provided to both the work unit Safety Officer and the EHS Department upon completion of the task. | End of calendar year + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Environmental / Regulatory Compliance Checklist | Environmental / Regulatory Compliance Checklist Review | Design phase of renovation / construction projects | Project Leaders and Professionals are to complete this form in eBuilder during design phase of OPP projects | N/A |  | OPP
Environmental Emergency Plan / Storage Tanks | PADEP Regulated Storage Tank inspection by PADEP | Varies | Certain PA DEP regulated storage tanks must have an inspection a PA DEP certified inspection as directed on storage tank registration | Life of equipment | http://www.dep.pa.gov/Business/Land/Tanks/Pages/Forms-and-Applications.aspx | Maintenance
Environmental Emergency Plans | Grease trap clean-out documentation | Varies | Removal of grease from grease traps must be documented. | End of calendar year + 3 years | N/A | Maintenance, Housing & Food Service
Environmental Emergency Plans | Hydraulic elevators (> 55 gallons) inspection | Quarterly | Visual inspection of hydraulic system for leaks | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/elevator_inspection_report.doc | Maintenance, Housing & Food Service | UP: Performed by OPP. Campuses: vendor performs
Environmental Emergency Plans | Oil interceptors & oil/water separators inspection | Semiannually | Inspect oil interceptors and/or oil/water separators at least semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing drums (> 55 gallons) inspection | Monthly | Visual inspection of oil containing drums | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_drum_inspection_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing transformers (> 55 gallons) inspection | Semiannually | Visual inspection of transformer for leaks | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/transformer_inspection_checklist_rev_5-17.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Other oil-filled equipment (> 55 gallons) inspection | Varies | Visual inspection for leaks (see EHERP requirements) | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service, Labs
Environmental Emergency Plans | Review and update EHERP plan | Annual - September | Review and update EHERP as needed (due to personnel or facility changes) and at least annually | Superseded/ updated + 1 year | http://ehs.psu.edu/environmental-emergency-plans/overview | Maintenance, Housing & Food Service, Director of Business Services, Laboratories
Environmental Emergency Plans | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/environmental_hazards_emergency_response_plan_self_audit.docx | Maintenance, Housing & Food Service, and other areas that have a pan
Environmental Emergency Plans | Spill kits | Varies | Maintain and re-stock spill kits in elevator mechanical rooms, laboratories, machine shops, kitchens, storage tank locations, and other areas that require spill response kits. | N/A | http://ehs.psu.edu/environmental-emergency-plans/overview | Any | replacement costs
Environmental Emergency Plans | Spill response training for hazardous materials, oils, and/or storage tanks | Annual | Provide EHERP training to affected employees annually | End of calendar year in which course ends or separation of employment + 30 years |  | Maintenance, Labs, Housing & Food Service
Environmental Emergency Plans | Tier II reporting (SARA) | Due March 1st | Report of any chemical (including road salt and other ice melting products) that exceeds the Threshold Planning Quantity, generally 10,000 pounds or more | Superseded/ outdated + 1 year | https://www.lipatts.pa.gov/Account/Login.aspx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Annual - June | Visual inspection of aboveground storage tanks; this is more comprehensive than the monthly inspection. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/annual_aboveground_storage_tank_inspection_checklist_ehs-064_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Monthly | Visual inspection of aboveground storage tanks; there are two forms, one for fuel/oil storage tanks and one for chemical storage tanks. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_aboveground_storage_tank_inspection_checklist_ehs-062_rev_5-21.docx | Maintenance
https://ehs.psu.edu/sites/ehs/files/monthly_chemical_aboveground_storage_tank_inspection_checklist_ehs-063_rev_5-21.docx
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Every 72 hours | Visual inspection for aboveground storage tanks of 21,000 gallons or greater | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/routine_aboveground_storage_tank_inspection_checklist_ehs-065_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Containment water release inspection | Varies | Visual inspection of rainwater captured by a containment facility prior to release | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/containment_water_release_inspection_checklist_ehs-067_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Observation of tank filling procedures | Varies | Observe and document filling of above- or below-ground tanks | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/product_delivery_observation_form_ehs-068_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | PADEP Regulated Storage Tank Registration | Annual | Certain PA DEP Regulated storage tanks must have an inspection by a PA DEP certified inspection as directed on storage tank registration. | Until superseded |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground storage tank annual inspection | Annual - June | Check of underground storage tank monitoring equipment by vendor | Life of equipment |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank facility inspection | Monthly | Underground tank facility general inspection | Varies by tank size |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank sump inspections | Monthly | Underground storage sump inspections where no monitor is present must be inspected monthly | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_underground_storage_tank_sunp_inspection_checklist_ehs-070_rev_5-21.docx | Maintenance
Environmental real estate assessment | Environmental due diligence | Prior to leasing / purchasing real estate | If pondering leasing/purchasing/accepting non-PSU real estate, follow Finance and Business Real Estate process. | N/A |  | OPP, campus leadership
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Excavation Safety (OPP) | Excavation Safety PA 1-Call | Prior to work | A PA 1 Call shall be completed prior to any excavation/earth disturbance | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection | Automatic Fire Suppression Systems | Varies | All Testing / Inspection / Maintenance in accordance with appropriate NFPA standard / FM Global Recommendations for specific system (Sprinkler / Gaseous Agent / Standpipe / Fire Pumps / Backflow Devices etc.) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention and Protection; OPP | Fire Protection Systems: Report Impairments | Onset and end of impairment | When fire safety systems (alarms, sprinklers, etc.) are impaired (such as due to electrical or water failure, or for repairs), report to FM Global and use the Red Tag system as appropriate. | Duration of impairment | https://www.fmglobal.com/products-and-services/education-and-training/client-learning-solutions/~/media/64C97CB2A7004C18BA3A938A610FF429.ashx | Maintenance, H&FS
Fire Prevention/Protection | Automatic Sprinkler System inspection | Monthly | Inspect locked control valves with electronic tamper switches monthly; record pressure readings; investigate if change of 10% or more. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System inspection | Weekly | Inspect locked control valves without electronic tamper switches weekly | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System main drain flow test | Annual | Test main drain flow annually (per NFPA 25) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System tamper switch test | Semiannually | Test Supervisory/Tamper switches semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System water flow alarm test | Quarterly | Test water flow alarms quarterly (per NFPA 25); | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Building Fire Department Connection inspection | Quarterly | Inspect building fire department connections to ensure clear access and operation | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Building Fire Protection Pumps | Weekly or Monthly | Start pump - no flow running (Churn) weekly for Diesel driven, monthly for electric pumps (per NFPA 25) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Building Fire Protection Pumps | Annual | Annual pump inspection and flow test (per NFPA 25) - full flow/performance test and inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Curb box valve inspection & test | Annual - October | Inspect cover for accessibility; fully close and then fully open valve | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Dry sprinkler/fire suppression systems | Annual - October | Check and maintain low point drains annually prior to freezing weather, and as needed to ensure all water is drained from system piping. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems dry pipe trip test | Annual | Conduct partial trip test annually | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems full flow trip test | Every 3 Years | Conduct full flow trip test | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems inspection | Weekly / Monthly | Inspect valves, ensure locks; inspect gauges and record pressures (weekly without tamper switch, monthly with tamper switch) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems test | Quarterly | Test water flow alarms quarterly (per NFPA 25); test priming water; test low air alarm | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Emergency generator test | Weekly | Start and verify proper operation | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention/Protection | Emergency lighting / illuminated exit signs | Varies | Monthly activation test to ensure automatic lighting operation; Annual power test | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire Alarm System inspection & test | Annual - October | Inspect, maintain, and test fire alarm systems in accordance with NFPA 72 Standard "National Fire Alarm and Signaling Code" by qualified individual (manual pull stations, heat/smoke detectors, back-up batteries, etc.) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire Hydrant testing | Annual | Flushing/testing of fire hydrant by water authority or campus staff | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Monthly | Monthly cleaning is required for cooking operations using solid-fuel-burning cooking appliances | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Quarterly | Quarterly cleaning is required for high-volume or high-smoke/grease cooking operations such as 24-hour cooking, charbroiling, or Wok cooking. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Semiannually - June & December | Cleaning of kitchen cooking exhaust devices (hoods, grease-removal devices, fans, ducts, etc.) at least semi-annually if grease accumulation is observed | Until superseded | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Fire Suppression System Inspection | Semiannually - June & December | Semi-annual inspection, maintenance and testing of fixed fire protection system (per NFPA 17A) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services | Costs vary
Fire Prevention/Protection | Fire safety - Vital Building Information | Annually | Pesticide storage buildings, if they catch fire, should not be extinguished with water as runoff would be toxic. Smoke can also be toxic. EHERP should include this information, and building should have appropriate signage. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Agriculture
Fire Prevention/Protection | Fire suppression system backflow protection | Annual | Conduct full-flow test in excess of the greatest sprinkler demand | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service | Vendor charge
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
Fire Prevention/Protection | Resident RA/GA training in fire safety | Annual - August | Fire safety training including fire extinguisher use, building evacuation, and fire prevention, for Resident Advisors, Resident Directors, and Graduate Advisors living in PSU housing | Residence Life Maintains | http://ehs.psu.edu/fire-prevention-and-protection/overview | Housing / Residence Life, Student Affairs
Fire Prevention/Protection | Smoke control system - Inspection / testing / maintenance | Varies | Ensure systems are maintained in operable condition and perform as designed. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hearing Conservation | Medical Surveillance - hearing tests | Annual | Annual hearing test for employees in Hearing Conservation Program | Records kept by Occupational Medicine | http://ehs.psu.edu/hearing-conservation/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Occ Med at UP; contracted providers at campuses.
Hearing Conservation | Training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Hearing Conservation | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring, exposure monitoring, and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene/ Laboratory Safety / Chemical Hygiene | Gas monitoring & alarms | As needed | Where gas monitors are installed or needed, follow procedures outlined in the Gas Monitoring Program. | See program | https://ehs.psu.edu/sites/ehs/files/gas_monitoring_program_-_final.docx | Labs, Engineering, Maintenance | Monitoring devices
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Laboratory Safety; OPP | Pressure vessel inspection | Annual | Annual inspection of pressure vessels (autoclaves, boilers, etc.) by Labor & Industry. Managed by Risk Management through FM Global. | Keep current version | N/A | OPP, Maintenance, Laboratories
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead in building materials | Assessment of Lead in other building materials (flashing, window camings, etc.) | Prior to demolition / work that affects lead-containing material | Contact EHS prior to any work that could affect lead-containing materials. This includes but is not limited to: lead flashing, window camings, lead-lined walls for X-ray suites, etc. | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, Residence Hall Housekeeping, OPP PMs, PCs, Designers | sampling and testing fees vary
Lead Paint | Assessment of lead paint in all maintenance, renovation or demolition that affects paint | Before maintenance, renovation or demolition that affects paint | Follow EHS / OPP Lead Paint Procedures | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP | Possible sampling and testing fees, depending scope and funding source.
Lead Paint | Assessment of lead paint in pre-1978 residential housing (non-undergraduate) and child-occupied facilities (e.g. daycare) | Before maintenance, renovation or demolition that affects paint | Contact EHS prior to any work that could affect paint. | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Lead Paint | Lead paint awareness training | Prior to initial exposure | Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality
Lockout/Tagout | LOTO Affected Personnel Training | Initial | Initial training for employees who do not perform LOTO but may be affected by equipment that is LOTO'd | End of calendar year in which course ends or separation of employment + 30 years | EHS - Lockout/Tagout Affected Employee Training | Maintenance, could be anyone
Lockout/Tagout | LOTO contractor notification forms | Prior to contractor beginning work | Work units must exchange LOTO procedures with contractors servicing/maintaining PSU equipment that requires LOTO. This form documents that information exchange. | End of calendar year + 1 year | https://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Lockout/Tagout | LOTO evaluation | Annual - July | Annual evaluation of all employees authorized to use Lockout/Tagout procedures | Period of employment in the work unit | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO lock removal form | As needed | Documentation of lock removal by anyone other than designated employee to whom lock is assigned | End of calendar year + 1 year |  | Maintenance, could be anyone
Lockout/Tagout | LOTO procedures | Initial and update as needed | Documented LOTO procedure is required for equipment with multiple energy sources | Life of equipment | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO training | Initial | Initial training for employees who perform Lockout/Tagout | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | http://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
PCB building materials | Assess for PCBs prior to all maintenance, renovation or demolition in / on pre-1980 facilities | Before maintenance, renovation or demolition. | Contact EHS before conducting maintenance, renovations or demolition in / on pre-1980 buildings. | Records retained by EHS | N/Ahttps://ehs.psu.edu/PCB-Containing%20Building%20Material%20Management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age. | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Pest Management | Integrated Pest Management plan review | Annually | If you have an Integrated Pest Management Plan, review it annually to ensure it is up to date and that program is being followed as provided by the plan. | Until superseded/ updated + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-integrated-pest-management | Maintenance, Housing and Food Services
Pesticides | Application records | Varies | Pesticide application records must be kept for the past 3 years. | Date of application + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Eyewash | Prior to use | For pesticides being mixed from concentrates, a flowing eyewash must be present in the area where the pesticide is mixed. If the pesticide label says eye protection is required, then the applicators must carry bottled eyewash with them.
Pesticides | Eyewash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Inventory | Annual - January | Annual pesticide inventory (in CHIMs) | Date of acquisition + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | License | Annual | Copies of the annual Certified Applicator License and the Pesticide Business License must be up-to-date and available. | Until superseded | N/A | Maintenance, Labs/farms/research using pesticides
Pesticides | Pesticide storage area inspection | Monthly | Inspect pesticide storage area | End of calendar year + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/pesticide_facility_annual_self_audit_0.docx | Maintenance, Housing & Food Service, Labs/farms/research using pesticides
Pesticides | Worker Protection Standard Training | Annual | All employees who are not certified applicators and who work in areas where pesticides are used for agricultural applications, including greenhouses, must take annual training. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs/farms/research using pesticides
Powered Industrial Trucks (forklifts) | PIT annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone | External inspector fee varies
Powered Industrial Trucks (forklifts) | PIT daily inspection | Daily | Documented by operator | End of calendar year + 1 year | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT hands-on user evaluation | Every 3 years | Hands-on evaluation required for PIT (forklift) operators | Period of employment in the work unit | https://ehs.psu.edu/pit/forms | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT inventory | Initial, review and update as needed | Each work unit is responsible for keeping a list of all PITs within the work unit. | Until superseded |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT repair records | As needed | Retain all repair records | Life of equipment |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT user training | Initial | Initial classroom & hands-on training for users of PITs (forklifts) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Powered Industrial Truck (Forklift) Training | Maintenance, could be anyone
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Refrigerant | Annual self-audit for appliance owners | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self-audit_for_appliance_owners.docx | Maintenance, Housing & Foods
Refrigerant | Annual self-audit for service providers | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self_audit_for_service_providers.docx | Maintenance, Housing & Foods
Refrigerant | Appliance Inventory | Annual - January | Inventory of all refrigeration units containing 50 or more pounds of circuit | Until superseded | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Certification | Initial | Maintain certification(s) for employees who use refrigerants | Period of employment in the work unit + 3 years | N/A | Maintenance, Housing & Foods
Refrigerant | Leak Rate Calculations | Varies | For all appliances containing 50 pounds or more of refrigerant, leak rates must be calculated each time refrigerant is added. There is a spreadsheet which performs these calculations. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Refrigerant Inventory | As needed | Keep a log of all refrigerant usage from purchase to return for reclamation | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Service records | Varies | Maintain required service records and submit them to the appliance owner, including all records referring to refrigerant used, removed, or reclaimed. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## M&O Campuses
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Asbestos | Asbestos assessment in equipment (e.g. fume hood liners, ovens, lab bench tops, etc.) | Before maintenance, repair or disposal | Contact EHS before maintenance, repair or disposal; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Asbestos | Asbestos assessment prior to any maintenance, renovation or demolition | Before maintenance, renovation or demolition. | Contact EHS before conducting any work in / on pre-1990 buildings. Exterior renovations such as roofing do not have a date cut-off; contact EHS before any exterior work. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Asbestos | Asbestos awareness training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/asbestos-management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality
Asbestos - Structural Demolition | Asbestos assessment prior to demolition or removal of structural members within a building | Before demolition or removal of structural members | Contact EHS before demolition or removal of structural members; there is no cut-off date for this. | Records retained by EHS | http://ehs.psu.edu/asbestos-management/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Possible sampling and testing fees, depending scope and funding source.
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (non-research) | Annual - May | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Bloodborne Pathogens Training | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Eyewash & shower testing (annual) | Annual - July | Annually test and inspect eyewashes and safety showers (this is currently performed by EHS) | EHS maintains records |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self-inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Laboratory Safety or Chemical and Waste Handling (non-labs) refresher training | Annual - August | Complete chemical and hazardous waste refresher training annually | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | N/A | Maintenance, Housing & Food Services, potentially other areas
Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
Confined Space | Confined Space Awareness training | Initial | Training recommended for employees who may work around Confined Spaces but will not be entering those spaces. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Permit | Prior to entry | Permit must be filled out and approved, and hazards must be identified and mitigated, prior to entering confined space | End of calendar year + 1 year | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Training | Initial | Training required for any employee who will be entering a Permit-Required Confined Space | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space inventory | Initial, and updated as needed | Keep an up-to-date list of confined spaces on each campus | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space labeling | Initial | Label all Permit-Required Confined Spaces | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | cost depends on sign type (~$10-150)
Confined Space | Confined Space Rescue | Prior to entry | Prior to entering a Permit-Required Confined Space, a Confined Space Rescue Team must be available and on-call (in-house or county EMS or provider) | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | CS rescue equipment costs at UP
Confined Space | Confined Space Rescue Training | Annual - June | In-house Confined Space Rescue Teams must be trained/refreshed at least once every 12 months | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Inform Contractors | Prior to entry | Inform contractors of confined spaces and any known hazards relevant to their scope of work and remind them that they must comply with OSHA Confined Space standards | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Contractor Safety (OPP) | Contractor safety (construction and non-construction) |  | See OPP contractor/construction safety requirements in Design & Construction standards Division 00. Note: This currently applies only to contractors hired by OPP. | N/A | https://wikispaces.psu.edu/download/attachments/357076600/PSU%20OPP%20Contractor_Safety_Requirements.pdf?version=2&modificationDate=1550257929000&api=v2 | Maintenance, Housing & Food Services, Information Technology
Cranes, Hoists & Slings | Crane/Hoist annual inspection | Annual - May | Annual "periodic" inspection of crane by vendor | Life of equipment | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone | Costs vary by crane type and vendor
Cranes, Hoists & Slings | Crane/hoist monthly inspection | Monthly | Monthly "frequent" inspection of crane by vendor or designated employee | End of calendar year + 3 years | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Daily inspection | Daily | Visual inspection of crane/hoist/sling prior to each use | N/A | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Hands-on user evaluation | Initial | Hands-on evaluation required for Bridge Crane operators | Period of employment in the work unit | https://ehs.psu.edu/crane-hoist-sling/forms | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Inventory | Initial, review and update as needed | A listing of all cranes and hoists | Until superseded | Section 8.1.1 of the Crain, Hoist Sling Program Document | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Cranes, Hoists & Slings Training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Cranes, Hoists & Slings | Sling Annual inspection | Annual - May | Annual inspection of sling by Competent Person | Life of equipment | http://ehs.psu.edu/crane-hoist-sling/overview | Maintenance, Engineering, Agriculture, could be anyone
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E annual evaluation | Annual - July | Annual evaluation of all employees authorized to perform electrical work (includes LOTO evaluation) | Period of employment in the work unit | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E contractor/host employer meeting | As needed | Document the Contractor / Host Employer meeting. | Superseded/ updated + 1 year |  | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E equipment/task-specific work plans | Initial, review and update as needed | Documentation containing information pertaining to each electrical task and its corresponding PPE requirements shall be maintained by the work unit. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E PPE & equipment inspections | Varies | Electrical safety equipment such as insulating gloves, covers, arc flash suits require inspection. See Appendix G of program for complete list of equipment and frequency | Life of equipment | http://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, could be anyone | Glove inspection ~$40 per pair, every 6 months.
Electrical Safety | Energized Electrical/ NFPA 70E Self-Review of devices | Annual - July | Self-review of electrical devices in laboratories for safety compliance, specifically for machinery >50V. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Engineering, Science labs, Arts | employee time
Electrical Safety | Energized Electrical/ NFPA 70E Training | Every 3 years | Initial classroom training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Energized Electrical/NFPA 70E Arc Flash Training | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E work permit | As needed | Copies of all energized electrical work permits (appendix A) must be provided to both the work unit Safety Officer and the EHS Department upon completion of the task. | End of calendar year + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Environmental / Regulatory Compliance Checklist | Environmental / Regulatory Compliance Checklist Review | Design phase of renovation / construction projects | Project Leaders and Professionals are to complete this form in eBuilder during design phase of OPP projects | N/A |  | OPP
Environmental Emergency Plan / Storage Tanks | PADEP Regulated Storage Tank inspection by PADEP | Varies | Certain PA DEP regulated storage tanks must have an inspection a PA DEP certified inspection as directed on storage tank registration | Life of equipment | http://www.dep.pa.gov/Business/Land/Tanks/Pages/Forms-and-Applications.aspx | Maintenance
Environmental Emergency Plans | Grease trap clean-out documentation | Varies | Removal of grease from grease traps must be documented. | End of calendar year + 3 years | N/A | Maintenance, Housing & Food Service
Environmental Emergency Plans | Hydraulic elevators (> 55 gallons) inspection | Quarterly | Visual inspection of hydraulic system for leaks | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/elevator_inspection_report.doc | Maintenance, Housing & Food Service | UP: Performed by OPP. Campuses: vendor performs
Environmental Emergency Plans | Oil interceptors & oil/water separators inspection | Semiannually | Inspect oil interceptors and/or oil/water separators at least semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing drums (> 55 gallons) inspection | Monthly | Visual inspection of oil containing drums | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_drum_inspection_checklist.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Oil-containing transformers (> 55 gallons) inspection | Semiannually | Visual inspection of transformer for leaks | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/transformer_inspection_checklist_rev_5-17.docx | Maintenance, Housing & Food Service
Environmental Emergency Plans | Other oil-filled equipment (> 55 gallons) inspection | Varies | Visual inspection for leaks (see EHERP requirements) | End of calendar year + 3 years | http://ehs.psu.edu/sites/ehs/files/monthly_oil-filled_equipment_checklist.docx | Maintenance, Housing & Food Service, Labs
Environmental Emergency Plans | Review and update EHERP plan | Annual - September | Review and update EHERP as needed (due to personnel or facility changes) and at least annually | Superseded/ updated + 1 year | http://ehs.psu.edu/environmental-emergency-plans/overview | Maintenance, Housing & Food Service, Director of Business Services, Laboratories
Environmental Emergency Plans | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/environmental_hazards_emergency_response_plan_self_audit.docx | Maintenance, Housing & Food Service, and other areas that have a pan
Environmental Emergency Plans | Spill kits | Varies | Maintain and re-stock spill kits in elevator mechanical rooms, laboratories, machine shops, kitchens, storage tank locations, and other areas that require spill response kits. | N/A | http://ehs.psu.edu/environmental-emergency-plans/overview | Any | replacement costs
Environmental Emergency Plans | Spill response training for hazardous materials, oils, and/or storage tanks | Annual | Provide EHERP training to affected employees annually | End of calendar year in which course ends or separation of employment + 30 years |  | Maintenance, Labs, Housing & Food Service
Environmental Emergency Plans | Tier II reporting (SARA) | Due March 1st | Report of any chemical (including road salt and other ice melting products) that exceeds the Threshold Planning Quantity, generally 10,000 pounds or more | Superseded/ outdated + 1 year | https://www.lipatts.pa.gov/Account/Login.aspx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Annual - June | Visual inspection of aboveground storage tanks; this is more comprehensive than the monthly inspection. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/annual_aboveground_storage_tank_inspection_checklist_ehs-064_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Monthly | Visual inspection of aboveground storage tanks; there are two forms, one for fuel/oil storage tanks and one for chemical storage tanks. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_aboveground_storage_tank_inspection_checklist_ehs-062_rev_5-21.docx | Maintenance
https://ehs.psu.edu/sites/ehs/files/monthly_chemical_aboveground_storage_tank_inspection_checklist_ehs-063_rev_5-21.docx
Environmental Emergency Plans / Storage Tanks | Aboveground storage tank inspection | Every 72 hours | Visual inspection for aboveground storage tanks of 21,000 gallons or greater | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/routine_aboveground_storage_tank_inspection_checklist_ehs-065_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Containment water release inspection | Varies | Visual inspection of rainwater captured by a containment facility prior to release | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/containment_water_release_inspection_checklist_ehs-067_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | Observation of tank filling procedures | Varies | Observe and document filling of above- or below-ground tanks | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/product_delivery_observation_form_ehs-068_rev_5-21.docx | Maintenance
Environmental Emergency Plans / Storage Tanks | PADEP Regulated Storage Tank Registration | Annual | Certain PA DEP Regulated storage tanks must have an inspection by a PA DEP certified inspection as directed on storage tank registration. | Until superseded |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground storage tank annual inspection | Annual - June | Check of underground storage tank monitoring equipment by vendor | Life of equipment |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank facility inspection | Monthly | Underground tank facility general inspection | Varies by tank size |  | Maintenance
Environmental Emergency Plans / Storage Tanks | Underground tank sump inspections | Monthly | Underground storage sump inspections where no monitor is present must be inspected monthly | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_underground_storage_tank_sunp_inspection_checklist_ehs-070_rev_5-21.docx | Maintenance
Environmental real estate assessment | Environmental due diligence | Prior to leasing / purchasing real estate | If pondering leasing/purchasing/accepting non-PSU real estate, follow Finance and Business Real Estate process. | N/A |  | OPP, campus leadership
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Excavation Safety (OPP) | Excavation Safety PA 1-Call | Prior to work | A PA 1 Call shall be completed prior to any excavation/earth disturbance | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety Training | Annual - March | Competent person excavation training for anyone who performs excavation activities | End of calendar year in which course ends or separation of employement, + 30 years | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Excavation Safety (OPP) | Excavation Safety trench inspection | Daily | A competent person shall complete a trench inspection daily, after a rainstorm, or if there is a hazardous condition | End of calendar year + 1 year | https://opp.psu.edu/sites/opp/files/excavation_safety_program.pdf | Maintenance, could be anyone
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection | Automatic Fire Suppression Systems | Varies | All Testing / Inspection / Maintenance in accordance with appropriate NFPA standard / FM Global Recommendations for specific system (Sprinkler / Gaseous Agent / Standpipe / Fire Pumps / Backflow Devices etc.) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention and Protection; OPP | Fire Protection Systems: Report Impairments | Onset and end of impairment | When fire safety systems (alarms, sprinklers, etc.) are impaired (such as due to electrical or water failure, or for repairs), report to FM Global and use the Red Tag system as appropriate. | Duration of impairment | https://www.fmglobal.com/products-and-services/education-and-training/client-learning-solutions/~/media/64C97CB2A7004C18BA3A938A610FF429.ashx | Maintenance, H&FS
Fire Prevention/Protection | Automatic Sprinkler System inspection | Monthly | Inspect locked control valves with electronic tamper switches monthly; record pressure readings; investigate if change of 10% or more. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System inspection | Weekly | Inspect locked control valves without electronic tamper switches weekly | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System main drain flow test | Annual | Test main drain flow annually (per NFPA 25) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System tamper switch test | Semiannually | Test Supervisory/Tamper switches semi-annually | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Automatic Sprinkler System water flow alarm test | Quarterly | Test water flow alarms quarterly (per NFPA 25); | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Building Fire Department Connection inspection | Quarterly | Inspect building fire department connections to ensure clear access and operation | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Building Fire Protection Pumps | Weekly or Monthly | Start pump - no flow running (Churn) weekly for Diesel driven, monthly for electric pumps (per NFPA 25) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Building Fire Protection Pumps | Annual | Annual pump inspection and flow test (per NFPA 25) - full flow/performance test and inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Curb box valve inspection & test | Annual - October | Inspect cover for accessibility; fully close and then fully open valve | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Dry sprinkler/fire suppression systems | Annual - October | Check and maintain low point drains annually prior to freezing weather, and as needed to ensure all water is drained from system piping. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems dry pipe trip test | Annual | Conduct partial trip test annually | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems full flow trip test | Every 3 Years | Conduct full flow trip test | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems inspection | Weekly / Monthly | Inspect valves, ensure locks; inspect gauges and record pressures (weekly without tamper switch, monthly with tamper switch) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Dry sprinkler/fire suppression systems test | Quarterly | Test water flow alarms quarterly (per NFPA 25); test priming water; test low air alarm | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Emergency generator test | Weekly | Start and verify proper operation | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention/Protection | Emergency lighting / illuminated exit signs | Varies | Monthly activation test to ensure automatic lighting operation; Annual power test | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire Alarm System inspection & test | Annual - October | Inspect, maintain, and test fire alarm systems in accordance with NFPA 72 Standard "National Fire Alarm and Signaling Code" by qualified individual (manual pull stations, heat/smoke detectors, back-up batteries, etc.) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire curtain - inspect / test / maintain | Varies | Maintain fire curtain in accordance with NFPA Standard 80. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Theater
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire Hydrant testing | Annual | Flushing/testing of fire hydrant by water authority or campus staff | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Monthly | Monthly cleaning is required for cooking operations using solid-fuel-burning cooking appliances | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Quarterly | Quarterly cleaning is required for high-volume or high-smoke/grease cooking operations such as 24-hour cooking, charbroiling, or Wok cooking. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Exhaust Inspection & Cleaning | Semiannually - June & December | Cleaning of kitchen cooking exhaust devices (hoods, grease-removal devices, fans, ducts, etc.) at least semi-annually if grease accumulation is observed | Until superseded | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
Fire Prevention/Protection | Fire Protection- Commercial Kitchen Cooking Fire Suppression System Inspection | Semiannually - June & December | Semi-annual inspection, maintenance and testing of fixed fire protection system (per NFPA 17A) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services | Costs vary
Fire Prevention/Protection | Fire safety - Vital Building Information | Annually | Pesticide storage buildings, if they catch fire, should not be extinguished with water as runoff would be toxic. Smoke can also be toxic. EHERP should include this information, and building should have appropriate signage. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Agriculture
Fire Prevention/Protection | Fire suppression system backflow protection | Annual | Conduct full-flow test in excess of the greatest sprinkler demand | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service | Vendor charge
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
Fire Prevention/Protection | Resident RA/GA training in fire safety | Annual - August | Fire safety training including fire extinguisher use, building evacuation, and fire prevention, for Resident Advisors, Resident Directors, and Graduate Advisors living in PSU housing | Residence Life Maintains | http://ehs.psu.edu/fire-prevention-and-protection/overview | Housing / Residence Life, Student Affairs
Fire Prevention/Protection | Smoke control system - Inspection / testing / maintenance | Varies | Ensure systems are maintained in operable condition and perform as designed. System performance testing/inspection/maintenance in accordance with appropriate National Fire Protection Association (NFPA) standard for type system. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Foods
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hazardous Materials Shipping | Hazardous Materials/Dangerous Goods Shipping Training | Every 2 Years | Individuals who ship hazardous materials (biological, chemical, radioactive, and/or waste) and sign paperwork must receive DOT/IATA and/or NRC training every other year. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Maintenance, Janitorial, Housing & Food Service, Police Services
Hazmat shipping: Import/Export permits (Ethics & Compliance) | HazMat Shipments - Import/Export Permits (TSCA) | Prior to shipping internationally | Refer to Ethics & Compliance website and the EHS Hazardous Materials shipping program for information on importing or exporting hazardous materials | EHS retains forms | https://universityethics.psu.edu/export-compliance | Any
Hearing Conservation | Medical Surveillance - hearing tests | Annual | Annual hearing test for employees in Hearing Conservation Program | Records kept by Occupational Medicine | http://ehs.psu.edu/hearing-conservation/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Occ Med at UP; contracted providers at campuses.
Hearing Conservation | Training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Hearing Conservation | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hand-Held Portable air monitoring equipment calibration | Annual; Fresh air tested or bump calibration prior to each use. | Portable air monitoring, exposure monitoring, and respiratory fit-testing equipment should be calibrated at least once every 12-24 months, or according to manufacturer's schedule, and bump-tested according to manufacturer's instructions. | Life of the equipment | See equipment manufacturer specifications | OPP, EHS, Maintenance, Housing & Food Services, IT Services | variable
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene / Chemical Hygiene / Lab Safety / Biosafety | Commissioning of fume hoods and biosafety cabinets | Initial | Commissioning of fume hoods by 3rd party (test reports) prior to first performance test and use | Archive/Storage by Project Team; Biosafety Cabinets additionally by User |  | Labs, Engineering. Maintenance | Costs vary by hood type and vendor
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene; Laboratory Safety; Chemical Safety | Nanotechnology hazard assessment | Initial and update annually | Plans to work with nanoparticles shall be discussed with EHS prior to commencing project. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/resources | Labs, Engineering, Art studios
Industrial Hygiene / Laboratory Safety/ Chemical Hygiene | Annual fume hood testing | Annual - as scheduled | Currently performed by EHS; could get pushed out to campuses/work units? | Archived by EHS, historically, transitioning to OPP for U/Park |  | Labs, Engineering. Maintenance
Industrial Hygiene / Laboratory Safety/ Chemical Hygiene | Gas monitoring & alarms | As needed | Where gas monitors are installed or needed, follow procedures outlined in the Gas Monitoring Program. | See program | https://ehs.psu.edu/sites/ehs/files/gas_monitoring_program_-_final.docx | Labs, Engineering, Maintenance | Monitoring devices
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Laboratory Safety; OPP | Pressure vessel inspection | Annual | Annual inspection of pressure vessels (autoclaves, boilers, etc.) by Labor & Industry. Managed by Risk Management through FM Global. | Keep current version | N/A | OPP, Maintenance, Laboratories
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead in building materials | Assessment of Lead in other building materials (flashing, window camings, etc.) | Prior to demolition / work that affects lead-containing material | Contact EHS prior to any work that could affect lead-containing materials. This includes but is not limited to: lead flashing, window camings, lead-lined walls for X-ray suites, etc. | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, Residence Hall Housekeeping, OPP PMs, PCs, Designers | sampling and testing fees vary
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Lead Paint | Assessment of lead paint in all maintenance, renovation or demolition that affects paint | Before maintenance, renovation or demolition that affects paint | Follow EHS / OPP Lead Paint Procedures | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP | Possible sampling and testing fees, depending scope and funding source.
Lead Paint | Assessment of lead paint in pre-1978 residential housing (non-undergraduate) and child-occupied facilities (e.g. daycare) | Before maintenance, renovation or demolition that affects paint | Contact EHS prior to any work that could affect paint. | Records retained by EHS | http://ehs.psu.edu/lead-based-paint/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Lockout/Tagout | LOTO Affected Personnel Training | Initial | Initial training for employees who do not perform LOTO but may be affected by equipment that is LOTO'd | End of calendar year in which course ends or separation of employment + 30 years | EHS - Lockout/Tagout Affected Employee Training | Maintenance, could be anyone
Lockout/Tagout | LOTO contractor notification forms | Prior to contractor beginning work | Work units must exchange LOTO procedures with contractors servicing/maintaining PSU equipment that requires LOTO. This form documents that information exchange. | End of calendar year + 1 year | https://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Lockout/Tagout | LOTO evaluation | Annual - July | Annual evaluation of all employees authorized to use Lockout/Tagout procedures | Period of employment in the work unit | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO lock removal form | As needed | Documentation of lock removal by anyone other than designated employee to whom lock is assigned | End of calendar year + 1 year |  | Maintenance, could be anyone
Lockout/Tagout | LOTO procedures | Initial and update as needed | Documented LOTO procedure is required for equipment with multiple energy sources | Life of equipment | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO training | Initial | Initial training for employees who perform Lockout/Tagout | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | http://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
OPP / Athletics | Building Code (PA) including bleacher safety | Every 3 years | Bleachers must be inspected by an external party at least once every 3 years per PA Dep't of Labor & Industry | Life of equipment | N/A | Athletics, Student Affairs | External inspector fee varies
OPP / Construction fencing | Construction fencing (Temporary & Worksite Barricading) | Duration of construction | Maintain appropriate fencing/barricading of construction worksites as outlined in OPP Design & Construction standard 01 50 00. | N/A | https://wikispaces.psu.edu/display/OPPDCS/01+50+00+TEMPORARY+FACILITIES+AND+CONTROLS | Maintenance, H&FS
PCB building materials | Assess for PCBs prior to all maintenance, renovation or demolition in / on pre-1980 facilities | Before maintenance, renovation or demolition. | Contact EHS before conducting maintenance, renovations or demolition in / on pre-1980 buildings. | Records retained by EHS | N/Ahttps://ehs.psu.edu/PCB-Containing%20Building%20Material%20Management/overview | Maintenance, Janitorial, HFS, OPP, ARL, Hospitality | Possible sampling and testing fees, depending scope and funding source.
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Pest Management | Integrated Pest Management plan review | Annually | If you have an Integrated Pest Management Plan, review it annually to ensure it is up to date and that program is being followed as provided by the plan. | Until superseded/ updated + 1 year | https://ehs.psu.edu/pesticide-management/pesticide-integrated-pest-management | Maintenance, Housing and Food Services
Pesticides | Application records | Varies | Pesticide application records must be kept for the past 3 years. | Date of application + 3 years | https://ehs.psu.edu/pesticide-management/pesticide-forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Eyewash | Prior to use | For pesticides being mixed from concentrates, a flowing eyewash must be present in the area where the pesticide is mixed. If the pesticide label says eye protection is required, then the applicators must carry bottled eyewash with them.
Pesticides | Eyewash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Maintenance, Labs/farms/research using pesticides
Pesticides | Inventory | Annual - January | Annual pesticide inventory (in CHIMs) | Date of acquisition + 1 year | http://ehs.psu.edu/sites/ehs/files/annual_pesticide_inventory_form.docx | Maintenance, Labs/farms/research using pesticides
Pesticides | License | Annual | Copies of the annual Certified Applicator License and the Pesticide Business License must be up-to-date and available. | Until superseded | N/A | Maintenance, Labs/farms/research using pesticides
Pesticides | Pesticide storage area inspection | Monthly | Inspect pesticide storage area | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/monthly_pesticide_facility_checklist_0.docx | Maintenance, Labs/farms/research using pesticides
Pesticides | Self-audit | Annual - January | Annual self-audit | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/pesticide_facility_annual_self_audit_0.docx | Maintenance, Housing & Food Service, Labs/farms/research using pesticides
Pesticides | Worker Protection Standard Training | Annual | All employees who are not certified applicators and who work in areas where pesticides are used for agricultural applications, including greenhouses, must take annual training. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs/farms/research using pesticides
Powered Industrial Trucks (forklifts) | PIT annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone | External inspector fee varies
Powered Industrial Trucks (forklifts) | PIT daily inspection | Daily | Documented by operator | End of calendar year + 1 year | http://ehs.psu.edu/pit/overview | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT hands-on user evaluation | Every 3 years | Hands-on evaluation required for PIT (forklift) operators | Period of employment in the work unit | https://ehs.psu.edu/pit/forms | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT inventory | Initial, review and update as needed | Each work unit is responsible for keeping a list of all PITs within the work unit. | Until superseded |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT repair records | As needed | Retain all repair records | Life of equipment |  | Maintenance, could be anyone
Powered Industrial Trucks (forklifts) | PIT user training | Initial | Initial classroom & hands-on training for users of PITs (forklifts) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Powered Industrial Truck (Forklift) Training | Maintenance, could be anyone
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/laboratory-safety/forms | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Refrigerant | Annual self-audit for appliance owners | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self-audit_for_appliance_owners.docx | Maintenance, Housing & Foods
Refrigerant | Annual self-audit for service providers | Annual - January | Annual self-audit of refrigerant program implementation | End of calendar year + 1 year | http://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_self_audit_for_service_providers.docx | Maintenance, Housing & Foods
Refrigerant | Appliance Inventory | Annual - January | Inventory of all refrigeration units containing 50 or more pounds of circuit | Until superseded | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Certification | Initial | Maintain certification(s) for employees who use refrigerants | Period of employment in the work unit + 3 years | N/A | Maintenance, Housing & Foods
Refrigerant | Leak Rate Calculations | Varies | For all appliances containing 50 pounds or more of refrigerant, leak rates must be calculated each time refrigerant is added. There is a spreadsheet which performs these calculations. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Refrigerant Inventory | As needed | Keep a log of all refrigerant usage from purchase to return for reclamation | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Refrigerant | Service records | Varies | Maintain required service records and submit them to the appliance owner, including all records referring to refrigerant used, removed, or reclaimed. | End of calendar year + 3 years | https://ehs.psu.edu/sites/ehs/files/refrigerant_management_program_forms_rev_2019_triggers.xlsx | Maintenance, Housing & Foods
Regulated Medical Waste | Regulated Medical Waste Pickup (Campuses) | Quarterly or more often as needed | Regulated medical waste cannot remain on campus more than 90 days. Details on handling are in policy SY29. | End of calendar year + 2 years | http://ehs.psu.edu/infectious-waste-management/overview | Laboratories, Nurses
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Theater Rigging | Theater Rigging Inspection (annual) | Annual - January | Documented inspection by a Competent Inspector is required annually | Life of equipment | https://ehs.psu.edu/theatre-rigging/forms | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (Third Party) | Every 3 years | Documented inspection by a third party (outside vendor) is required every 3 years. | Life of equipment | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (visual) | Prior to Use | Rigging must be visually inspected before each use | N/A | https://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspector training | Initial | Training is required for Competent inspectors of theatrical rigging. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Repair Records | As needed | Retain all repair records | Life of equipment |  | Maintenance, Theater Department faculty/staff
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Police
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (non-research) | Annual - May | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Bloodborne Pathogens Training | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Emergency Evacuations & Fire Drills- Residence Halls | Monthly | Fire Drills are required in Residence Halls monthly when classes are in session | End of calendar year + 7 years | https://policy.psu.edu/policies/sy28 | Residence Life, Police Services, Housing
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Confined Space | Confined Space Awareness training | Initial | Training recommended for employees who may work around Confined Spaces but will not be entering those spaces. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Permit | Prior to entry | Permit must be filled out and approved, and hazards must be identified and mitigated, prior to entering confined space | End of calendar year + 1 year | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space Entry Training | Initial | Training required for any employee who will be entering a Permit-Required Confined Space | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space inventory | Initial, and updated as needed | Keep an up-to-date list of confined spaces on each campus | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Confined Space labeling | Initial | Label all Permit-Required Confined Spaces | Until superseded | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | cost depends on sign type (~$10-150)
Confined Space | Confined Space Rescue | Prior to entry | Prior to entering a Permit-Required Confined Space, a Confined Space Rescue Team must be available and on-call (in-house or county EMS or provider) | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas | CS rescue equipment costs at UP
Confined Space | Confined Space Rescue Training | Annual - June | In-house Confined Space Rescue Teams must be trained/refreshed at least once every 12 months | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Confined Space | Inform Contractors | Prior to entry | Inform contractors of confined spaces and any known hazards relevant to their scope of work and remind them that they must comply with OSHA Confined Space standards | N/A | http://ehs.psu.edu/confined-space/overview | OPP, Maintenance, Housing & Food Services, University Police, Information Technology Services, School of Agriculture, ARL, and some research areas
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire Alarm System inspection & test | Annual - October | Inspect, maintain, and test fire alarm systems in accordance with NFPA 72 Standard "National Fire Alarm and Signaling Code" by qualified individual (manual pull stations, heat/smoke detectors, back-up batteries, etc.) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Annual | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hearing Conservation | Medical Surveillance - hearing tests | Annual | Annual hearing test for employees in Hearing Conservation Program | Records kept by Occupational Medicine | http://ehs.psu.edu/hearing-conservation/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Occ Med at UP; contracted providers at campuses.
Hearing Conservation | Training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Hearing Conservation | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Student Affairs
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (non-research) | Annual - May | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Bloodborne Pathogens Training | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Emergency Evacuations & Fire Drills- Residence Halls | Monthly | Fire Drills are required in Residence Halls monthly when classes are in session | End of calendar year + 7 years | https://policy.psu.edu/policies/sy28 | Residence Life, Police Services, Housing
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
Fire Prevention/Protection | Resident RA/GA training in fire safety | Annual - August | Fire safety training including fire extinguisher use, building evacuation, and fire prevention, for Resident Advisors, Resident Directors, and Graduate Advisors living in PSU housing | Residence Life Maintains | http://ehs.psu.edu/fire-prevention-and-protection/overview | Housing / Residence Life, Student Affairs
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | EHS and work unit retains documentation until superseded / updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Multiple EHS programs | Boating Safety Training | Initial | Boating safety training is required by PA Fish & Boat Commission | End of calendar year in which course ends or separation of employment + 30 years | https://www.boat-ed.com/pennsylvania/ | Academics/Research
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
OPP / Athletics | Building Code (PA) including bleacher safety | Every 3 years | Bleachers must be inspected by an external party at least once every 3 years per PA Dep't of Labor & Industry | Life of equipment | N/A | Athletics, Student Affairs | External inspector fee varies
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Student Health
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Biosafety; ABS / H&FS | Food safety | As needed | Student requests for Bake Sales and other homemade food events must be approved by EHS. Housing & Foods and Risk Management may also be involved. | N/A |  | Student Affairs
Bloodborne Pathogen | Bloodborne Pathogen Hepatitis B Vaccination | Initial | Offer Hepatitis B vaccination to at risk employees. Occupational Medicine will retain vaccination records. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/bloodborne-pathogen/overview | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services | ~$100 per employee
Bloodborne Pathogen | Bloodborne Pathogen training (non-research) | Annual - May | Complete before working with blood or other potentially infectious materials. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Bloodborne Pathogens Training | Janitorial, Nurses, Labs, Athletics, Police, Housing & Food Services
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Emergency Evacuations & Fire Drills- Residence Halls | Monthly | Fire Drills are required in Residence Halls monthly when classes are in session | End of calendar year + 7 years | https://policy.psu.edu/policies/sy28 | Residence Life, Police Services, Housing
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Confined Space | Air monitoring equipment Calibration | Monthly | Calibrate atmospheric monitoring equipment (such as 4-gas meters) monthly, and bump-test before use. INET contracted units support automated bump test and calibration. Some other meters can be set to automatically calibrate monthly and bump-test nightly. | Life of equipment OR, if used to continuously monitor known contaminant as IDLH risk, employment + 30 years | http://ehs.psu.edu/confined-space/overview | Ag Sciences, OPP, M & O, Housing & Food Services, Information Technology Services, School of Agriculture, ARL, and some research areas, Engineering Labs, Student Affairs | Industrial Scientific Ventis unit ~ $1200/year
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Emergency Management | Crisis/Disaster Planning & Clery Exercises | Annual | Emergency Management and EHS should both be involved in campus disaster/crisis planning. | N/A | https://police.psu.edu/about-emergency-management
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
Fire Prevention/Protection | Resident RA/GA training in fire safety | Annual - August | Fire safety training including fire extinguisher use, building evacuation, and fire prevention, for Resident Advisors, Resident Directors, and Graduate Advisors living in PSU housing | Residence Life Maintains | http://ehs.psu.edu/fire-prevention-and-protection/overview | Housing / Residence Life, Student Affairs
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | End of calendar year in which monitoring performed/record +30 years |  | All except Classroom and Office
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | EHS and work unit retains documentation until superseded / updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Multiple EHS programs | Boating Safety Training | Initial | Boating safety training is required by PA Fish & Boat Commission | End of calendar year in which course ends or separation of employment + 30 years | https://www.boat-ed.com/pennsylvania/ | Academics/Research
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
OPP / Athletics | Building Code (PA) including bleacher safety | Every 3 years | Bleachers must be inspected by an external party at least once every 3 years per PA Dep't of Labor & Industry | Life of equipment | N/A | Athletics, Student Affairs | External inspector fee varies
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All

## Theatre
EHS Program or other Department Overseeing | Compliance requirement | Frequency & Suggested Month | Instructions | Records Retention Requirement | Link | Departments Typically Affected | Associated Costs | Work Unit Person Responsible | Work Unit Backup Person
AED | AED Approval letter | Initial | A formal approval letter is sent to the work unit once the AED serial number is acquired. | Until superseded/ updated + 1 year | N/A | Any/all
AED | AED Inspection (non UPark locations) | Monthly | Monthly inspection of AED, battery, pads, etc. | End of calendar year + 3 years | http://ehs.psu.edu/automated-external-defibrillator-aed/overview | Any/all | Non-UP- Employee Time; UP - ~$20/mo/unit
AED | Application to acquire and install an AED (Formerly known as the AED Work Plan) | Initial | A work unit must apply to have an AED installed/purchased. Customer Record would be the approval letter. | N/A | https://ehs.psu.edu/sites/ehs/files/form_-_application_to_aquire_and_install_an_aed.pdf | Any/all | If required to fund unit - Initial purchase cost ~$1200-$2000, replacement parts expense (pads $100, battery $150), monthly inspection cost (~$20/mo - UP)
AED | CPR/AED training | Every 2 years | Each building with an AED must have at least two employees trained to use the AED and perform CPR. | End of calendar year in which course ends or separation of employment + 30 years | N/A | Any/all | ~$80 per person
Aerial/Scissor Lifts | Aerial/Scissor Lift daily inspection | Prior to Use | Documented by operator | End of calendar year + 1 year | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift Inventory | Initial and update as needed | Each work unit is responsible for keeping a list of all lifts within the work unit. | Until superseded |  | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift repair records | As needed | Retain all repair records | Life of equipment | N/A | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lift training | Initial | Initial classroom & hands-on | End of calendar year in which course ends or separation of employment + 30 years | EHS - Aerial Lift/Boom Types of Lifts | Maintenance, Athletics, could be anyone
Aerial/Scissor Lifts | Aerial/Scissor Lifts annual inspection | Annual - November | Annual inspection performed by vendor | Life of equipment | https://ehs.psu.edu/sites/ehs/files/aerial_and_scissor_lift_safety_program.docx | Maintenance, Athletics, could be anyone | Outside vendor charges may vary
Aerial/Scissor Lifts | Aerial/Scissor Lifts user evaluation | Every 3 Years | Evaluation of all certified operators | Period of employment in the work unit | https://ehs.psu.edu/aerial-scissor-lifts/forms | Maintenance, Athletics, could be anyone
Building Emergency Evacuation Plan | Building Emergency Evacuation Plan Review | Annual - August | Written evacuation plans must be reviewed and updated annually. | Until superseded/ updated + 1 year | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Evacuation Exercises (Fire Drills) | Annual - August / September | Buildings that meet the mandatory exercise criteria, as defined in Appendix D of the Building Emergency Evacuation Program, are required to conduct an evacuation exercise of the building annually. See Appendix D and the BEEP program for more information and documentation form. | End of calendar year + 3 years | http://ehs.psu.edu/building-emergency-evacuation-program/overview | All
Building Emergency Evacuation Plan | Self-review | Annual - October | Complete the Annual Self-Review form annually to show that the written BEEP has been reviewed and updated. | End of calendar year + 1 year | https://ehs.psu.edu/building-emergency-evacuation-program/forms | All
Chemical Inventory Management | Chemical Inventory Update | Annual - June | Enter chemical inventory into CHIMS database; review and update inventory annually. Print a copy to be kept in Unit Specific Plan (labs) or (other areas). | Date of acquisition + 1 year | http://ehs.psu.edu/chemical-inventory-management/overview | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste; OPP Utilities | Drain Disposal (University Sanitary Systems) Safety Assessment | Prior to disposal | Persons seeking to drain-dispose chemicals that are not hazardous but are also not typical "gray water" (including but not limited to swimming pool/hot tub water; Syndaver storage water; gray water from use of specialty cleaners, etc.) must seek approval from EHS and OPP Utility Systems at UP. At campuses, approval must also be sought from the local wastewater treatment plant. | Retain email or approval letter, or note date of phone call and who approved. | https://policy.psu.edu/policies/sy40 | Any
Chemical/Hazardous Waste | Chemical and Waste Handling (non-labs) initial training | Initial | Complete initial training within 90 days of hire. Training intended for people who work with chemicals, but not in a laboratory setting. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Chemical Waste Management Training | Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Satellite Accumulation Area | Weekly | Complete inspection form weekly | End of calendar year + 3 years | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Any
Chemical/Hazardous Waste | Chemical Waste Pickup | Semiannually, June & December (for campuses) | Chemical waste cannot be kept for more than 12 months. Submit pickup requests in a timely fashion. At Non-UP locations, keep a copy of the waste manifest on site for 3 years, then return it to EHS. | Non-UP - Retain for 3 years | https://ehs.psu.edu/waste-disposal | Any
Chemical/Hazardous Waste | Eye wash inspection (weekly) | Weekly | Flush eye wash for 30 seconds and make sure it is functioning properly | N/A | https://ehs.psu.edu/chemical-and-hazardous-waste-management/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Lab Self Inspection | Annual | Complete annual lab self inspection (labs only) in January | End of calendar year + 1 year | http://ehs.psu.edu/laboratory-safety/forms | Labs, Art Studios, Maintenance, Janitorial, Housing & Food Service
Chemical/Hazardous Waste | Universal Waste Pickup | Annual - August | Universal Waste (batteries other than alkaline, fluorescent lamps, mercury-containing lamps or devices, ballasts, etc.) must be removed from campus at least once annually. | Non-UP - Retain for 3 years | N/A | Maintenance, Housing & Food Services, potentially other areas
Disabilities Services office | ADA Compliance Guidance | Prior to construction | Contact ADA office for assistance regarding ADA compliance | N/A | https://affirmativeaction.psu.edu/welcome/access-disability/ | Any
Driver Safety | Driver safety training | Initial | Employees between the ages of 18 and 21 must complete the driver safety training course if they are required to drive in the course of their employment. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/driver-safety/overview | Any/all
Driver Safety / Fleet Services | 15-passenger van training | Initial | Training is required for drivers of 15-passenger vans (whether rented from Fleet or from an outside vendor) | End of calendar year in which course ends or separation of employment + 30 years | https://transportation.psu.edu/driver-qualifications-and-responsibilites | Any/all
EHS/Risk Management | Student Clubs & Events | As needed | Follow Risk Management & EHS guidelines for student events, and seek approval for novel events. | Duration of event |  | Student Affairs
Electrical Safety | Circuit Breaker Panel Operator Training | Every 3 years | Anyone who flips breaker switches must have training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Electrical Disconnect Operation Safety | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E annual evaluation | Annual - July | Annual evaluation of all employees authorized to perform electrical work (includes LOTO evaluation) | Period of employment in the work unit | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E contractor/host employer meeting | As needed | Document the Contractor / Host Employer meeting. | Superseded/ updated + 1 year |  | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E equipment/task-specific work plans | Initial, review and update as needed | Documentation containing information pertaining to each electrical task and its corresponding PPE requirements shall be maintained by the work unit. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E PPE & equipment inspections | Varies | Electrical safety equipment such as insulating gloves, covers, arc flash suits require inspection. See Appendix G of program for complete list of equipment and frequency | Life of equipment | http://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, could be anyone | Glove inspection ~$40 per pair, every 6 months.
Electrical Safety | Energized Electrical/ NFPA 70E Self-Review of devices | Annual - July | Self-review of electrical devices in laboratories for safety compliance, specifically for machinery >50V. | Superseded/ updated + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Engineering, Science labs, Arts | employee time
Electrical Safety | Energized Electrical/ NFPA 70E Training | Every 3 years | Initial classroom training | End of calendar year in which course ends or separation of employment + 30 years | EHS - Energized Electrical/NFPA 70E Arc Flash Training | Maintenance, could be anyone
Electrical Safety | Energized Electrical/ NFPA 70E work permit | As needed | Copies of all energized electrical work permits (appendix A) must be provided to both the work unit Safety Officer and the EHS Department upon completion of the task. | End of calendar year + 1 year | https://ehs.psu.edu/energized-electrical-safety/forms | Maintenance, could be anyone
Emergency Eyewash and Safety Shower Guidance Resource | Ensure eyewash and/or safety shower is unobstructed and will not affect any nearby hazards (electrical equipment, chemical storage). Ensure signage present if location is not readily apparent. | Weekly/ as needed | The eyewash/shower must be clearly accessible. It must be 6-feet or more from electrical hazards. Chemicals shall not be stored under/near eyewashes or showers. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | Provide access and use training to any new employees/ students exposed to hazards that might warrant use of eyewash/shower | Initial, when a new individual is exposed to hazardous materials | PIs/Supervisors must show employees where eyewashes / showers are located and how to use them (if they have exposure to materials that may warrant their use). | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | N/A | PI/Supervisor | PI/Supervisor delegate
Emergency Eyewash and Safety Shower Guidance Resource | If using corrosive material, verify and eyewash and safety shower is immediately accessible within the work area (eyewash required for BSL1 labs). | Initial, when hazardous material introduced to work area | Contact EHS for access and location assessment. | N/A | N/A | Academic/ research departments; Work units with exposure to corrosive or biological hazards; Shop or industrial spaces | New eyewash /shower combo-unit is about $3,000 – 6,000 | PI/Supervisor | PI/Supervisor delegate
Ergonomics | Material handling (heavy lifting) training | Initial | Employees whose job includes heavy lifting should be trained in proper lifting techniques and use of appropriate lifting tools | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ergonomics/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Ergonomics | Workstation ergonomics training | As requested | Work units interested in workstation ergonomic training can schedule with EHS. | N/A | https://ehs.psu.edu/ergonomics/overview | All
Fall Protection | Fall Protection equipment annual inspection | Annual - May | Annual inspection of fall protection equipment (harnesses, lanyards, etc.) by vendor or designated employee (Competent Person) | Life of equipment | https://ehs.psu.edu/fall-protection/forms | Maintenance, could be anyone
Fall Protection | Fall Protection equipment competent inspector training | Initial | Fall protection equipment Competent Inspector training for those who will inspect fall protection equipment for their work unit | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection equipment pre-use inspection | Daily | Visual inspection of fall protection equipment prior to each use | N/A | http://ehs.psu.edu/fall-protection/overview | Maintenance, could be anyone
Fall Protection | Fall Protection installation annual inspection | Annual - May | Annual inspection of fall protection anchor/tie-off points and lifelines by vendor or designated employee (Competent Person) | Life of equipment |  | Maintenance, could be anyone | External inspector fee varies
Fall Protection | Fall Protection Training | Initial | Fall protection equipment training for those required to use harness, lanyard, etc. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Fall Protection | Maintenance, could be anyone
Fire Prevention & Protection / Emergency Management | Event considerations - public assembly emergency planning | Prior to event | Prior to an event, consult the guidelines for Event Fire Safety and the Pre-Event Safety Checklist. | N/A | https://ehs.psu.edu/fire-prevention-and-protection/guidelines | Any
Fire Prevention/Protection | Code compliance - occupancy limits | Prior to room setup | Prior to setting up a room for an event, consult occupancy limits per fire code. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance
Fire Prevention/Protection | Corridor storage | Daily | Corridors and stairwells shall not be used for storage. | N/A | https://policy.psu.edu/policies/sy36 | All
Fire Prevention/Protection | Events involving fire require EHS approval | Prior to event | Any event involving open fire must be approved in advance by EHS, Municipality, and Director of Business if at a Commonwealth Campus. | Duration of event | https://policy.psu.edu/policies/sy13 | Maintenance, Police & Public Safety, Risk Management, Student Affairs, EHS, Municipality
https://policies.psu.edu/policies/sy30
Fire Prevention/Protection | Fire curtain - inspect / test / maintain | Varies | Maintain fire curtain in accordance with NFPA Standard 80. | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Theater
Fire Prevention/Protection | Fire extinguisher inspection | Annual - October | Annual maintenance and inspection (per NFPA 10) (usually provided by a third party) | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher inspection | Monthly | Monthly visual inspection | End of calendar year + 3 years | http://ehs.psu.edu/fire-prevention-and-protection/overview | Maintenance, Housing & Food Service, Police Services
Fire Prevention/Protection | Fire extinguisher training | Initial | Recommended for H&FS personnel, laboratory personnel, and personnel who perform Hot Work; available to all | End of calendar year in which course ends or separation of employment + 30 years | EHS - Portable Fire Extinguisher Training | Any
Fire Prevention/Protection | Fire incident investigations | As needed | If a fire occurs, contact EHS and Risk Management, Police and Public Safety. | N/A | http://ehs.psu.edu/fire-prevention-and-protection/overview | All
Fire Prevention/Protection | Fireworks plan review | Prior to event | Any event involving fireworks must be approved in advance by EHS | N/A | https://ehs.psu.edu/fire-prevention-and-protection/resources | Student Affairs, Athletics, Events
First Aid Kits (SY21) | First aid kit inspection | Quarterly | Per SY21, First Aid kits must be inspected quarterly, and expired items must be removed. List of permissible contents is in SY21. | N/A | https://policy.psu.edu/policies/sy21 | Any
Hazard Communication | Hazard Communication training (on-line) | Initial | Initial classroom HazCom/Globally Harmonized System training. (For laboratories, this is included in the Laboratory Safety (initial) training.) | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Hazard Communication training (site-specific) | Initial | Unit/site-specific training on hazard communication, chemical storage locations, and chemical safety | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/hazcom/resources | Anyone using any sort of chemical (including lubricants and cleaners)
Hazard Communication | Review & update SDS collection for chemical inventory | Annual - May | Review Safety Data Sheets to ensure that SDS list matches CHIMS list, and that both the CHIMS list and the SDS list match the actual chemical inventory of the work unit | Superseded/ outdated + 30 years | https://ehs.psu.edu/hazcom/overview | Anyone using any sort of chemical (including lubricants and cleaners)
Hazardous materials | Inspection of items for disposal via Lion Surplus | Prior to sending to Lion Surplus | Items destined for Lion Surplus must be inspected for certain hazardous materials; see protocol on-line and consult EHS with questions. | NA | https://ehs.psu.edu/sites/ehs/files/lion_surplus_guidance_7-18.docx | Any
Hazardous Materials Shipping | Hazardous Materials/Dangerous Goods Shipping Training | Every 2 Years | Individuals who ship hazardous materials (biological, chemical, radioactive, and/or waste) and sign paperwork must receive DOT/IATA and/or NRC training every other year. | End of calendar year in which course ends or separation of employment + 30 years |  | Labs, Maintenance, Janitorial, Housing & Food Service, Police Services
Hazmat shipping: Import/Export permits (Ethics & Compliance) | HazMat Shipments - Import/Export Permits (TSCA) | Prior to shipping internationally | Refer to Ethics & Compliance website and the EHS Hazardous Materials shipping program for information on importing or exporting hazardous materials | EHS retains forms | https://universityethics.psu.edu/export-compliance | Any
Hearing Conservation | Medical Surveillance - hearing tests | Annual | Annual hearing test for employees in Hearing Conservation Program | Records kept by Occupational Medicine | http://ehs.psu.edu/hearing-conservation/overview | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc. | Occ Med at UP; contracted providers at campuses.
Hearing Conservation | Training | Annual | Complete training on PSU LRN system. Employees must complete video based portion AND review PSU specific supplemental materials (Microsoft Word Document) | End of calendar year in which course ends or separation of employment + 30 years | EHS - Hearing Conservation | OPP, HFS, Ag, Engineering, Labs, IT, Hospitality, Airport, ARL, Police, etc.
Hot Work | Hot work permit | As needed | A Hot Work Permit must be filled out and all procedures observed for any temporary operations involving the use of open flames or which can produce heat and/or sparks, including but not limited to welding, brazing, and soldering. | End of calendar year + 1 year | http://ehs.psu.edu/hot-work/forms | Maintenance, Engineering, Art Studios, could be anyone
Hot Work | Hot work training | Initial | Personnel who will perform hot work must be trained in the Hot Work program. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/hot-work/overview | Maintenance, Engineering, Art Studios, could be anyone
https://ehs.psu.edu/training?combine=&tid=121
Human Resources / Occupational Medicine / Risk Management | Report employee injuries | As they occur | Injuries to employees should be reported via the on-line system. Injuries resulting in hospitalization, amputation, eye damage, or other serious injuries or death must be reported to EHS within 8 hours. | Maintained by HR/Occupational Medicine | https://hr.psu.edu/workers-compensation | All
Human Resources / Occupational Medicine / Risk Management | Report student/visitor injuries | As they occur | Injuries to students or visitors should be reported using Risk Management's form, which should be emailed to Risk Management and cc'd to EHS. | Maintained by Risk Management | https://controller.psu.edu/claims | All
Indoor Air Quality | IAQ investigations | As needed | For indoor air quality concerns (including but not limited mold and odors), follow EHS's safety procedures, and enlist EHS and OPP assistance as needed. | N/A | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Indoor Air Quality | Water damage and mold - safety procedures | As needed | For water incursions and significant mold growth incidents, follow EHS's safety procedures, and enlist EHS assistance as needed. Contact OPP Service Desk (814-865-4731) for water incursion incidents at University Park campus. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/indoor-air-quality/requirements-guidelines | All
Industrial Hygiene | Exposure monitoring pumps or equipment | Prior to and following each use, or per manufacturer instructions. | Exposure monitoring samplers such as personal sampling pumps and real-time personal or area samplers to measure worker exposure | Notate Exposure Record with calibration information, OR calibration record maintained with Exposure Records. | See equipment manufacturer specifications | All
Industrial Hygiene | Exposure Records | N/A | Pertinent records, tables or reports which describe an employee's exposure should be retained in accordance with 1910.1020 | 30 years past the year generated. |  | All except Classroom and Office
Industrial Hygiene | Hazard Assessment | As initiated | Workplace and research operations to perform initial hazard assessment to determine whether exposure monitoring may be required. Documentation pertinent to program requirements. | Dependent on applicable OSHA standards or programmatic requirements |  | All except Classroom and Office
Industrial Hygiene | Industrial Hygiene exposure assessment | Prior to beginning work | Complete a hazard assessment prior to beginning work with materials that pose an exposure hazard - including but not limited to lead, hexavalent chromium, cadmium, formaldehyde, benzene, methylene chloride. See full list at website listed. | Until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/requirements-guidelines | All except classroom and office
Industrial Hygiene / Chemical Hygiene / Lab Safety / Biosafety | Commissioning of fume hoods and biosafety cabinets | Initial | Commissioning of fume hoods by 3rd party (test reports) prior to first performance test and use | Archive/Storage by Project Team; Biosafety Cabinets additionally by User | OPP Design and Construction Standards- D&C Standards (23.00.10.12) Lab Vent Systems | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene; Laboratory Safety; Chemical Safety | 3D printing pre-installation hazard assessment | Initial and update annually | 3D printer installations shall be discussed with EHS prior to commencing project or use. | EHS and work unit retains documentation until superseded / updated + 1 year | https://ehs.psu.edu/sites/ehs/files/3d_printing_hs_guide_11-16-2016.docx | Labs, Engineering, Art studios, Libraries, IT
Industrial Hygiene / Laboratory Safety / Chemical Hygiene | Annual fume hood testing | Annual - as scheduled | Transitioned to OPP | EHS and work unit retains documentation until superseded / updated + 1 year |  | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Industrial Hygiene / Laboratory Safety / Chemical Hygiene | Carcinogen hazard assessment and substance-specific control plans, as applicable, where determined necessary by initial exposure assessment | Initial and update annually | Wherever determined necessary by exposure level, or where required by OSHA regulation, substance-specific control plans shall be prepared. Use of carcinogens (including but not limited to materials regulated by individual OSHA substance-specific standards (e.g. formaldehyde, beryllium, arsenic, hexavalent chromium, cadmium, benzene, etc.) and similar highly hazardous materials must undergo a hazard assessment prior to work commencing. Engineering controls shall be used whenever possible. | EHS retains forms until superseded/ updated + 1 year | https://ehs.psu.edu/industrial-hygiene-exposure-recognition-control/forms | Ag Sciences, Art Studios, Bio Labs, Chem Labs, Engineering Labs, Student Health and Theatre
Integrated Safety Plan | Campus safety committee meeting | Quarterly or monthly | Campus Safety Committees should meet at least quarterly (monthly is recommended) | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | ISP team meetings | Quarterly | ISP teams should meet at least quarterly | End of calendar year + 3 years | http://ehs.psu.edu/integrated-safety-plan/overview | Any/all
Integrated Safety Plan | Self-review | Annual - February | Complete the ISP Self-Review Part I to establish your ISP team, then ISP Self-Review II annually thereafter to maintain ISP eligibility | Until superseded/ updated + 1 year | http://ehs.psu.edu/integrated-safety-plan/self-review | Any/all
Laboratory Safety | Safe and proper chemical storage | Ongoing | Reference chemical SDS and the Laboratory & Research Safety Plan regarding proper storage of chemicals. Consult EHS for assistance if needed. | N/A | https://ehs.psu.edu/sites/ehs/files/lab_and_research_safety_plan_-_v9.docx | Any
Laboratory Safety/ Occupational Safety/ Industrial Hygiene/ Chemical Hygiene | Compressed gas cylinder safety | Upon receipt of gas cylinder | Follow safety procedures outlined in SY 25 | N/A | https://policy.psu.edu/policies/sy25 | Any | Cylinder anchoring device prices vary (~$50-200+)
Ladder Safety | Ladder Inspection | Annual - March | All ladders must be inspected annually and the inspection documented on a decal on the ladder. | Life of equipment | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_b_0.docx | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Ladder Training | Initial | All personnel who use ladders must complete the ladder safety training. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Ladder Safety | Maintenance, Janitorial, Residence Hall Housekeeping, IT Services, Engineering, may be others
Ladder Safety | Stepstool Training | Initial | All personnel who use stepstools but not regular ladders must review the Step Stool Safety Awareness document. | N/A | https://ehs.psu.edu/sites/ehs/files/psu_ladder_program_app_e.docx | Libraries, Offices, Labs
Laser Safety | Annual laser self-inspection | Annual - February | Each lab must complete an annual laser self-inspection. Note that this includes inspection of interlocks, among other safety items. | End of calendar year + 1 year | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser registration | Initial | Class 3B and 4 lasers (including embedded lasers) must be registered with EHS | Until superseded | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety | Laser training | Initial | Users of Class 3B or 4 lasers (including embedded lasers) AND laser cutters must complete EHS and equipment specific training | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/laser-safety/overview | Labs with lasers
Laser Safety; Machine Shop Safety; Industrial Hygiene | Laser cutters hazard assessment | Initial | Consult EHS prior to installing laser cutters. Note that all applicable laser safety, machine shop safety, and industrial hygiene program items apply. Laser cutter users are also required to complete laser safety training. | N/A | https://ehs.psu.edu/sites/ehs/files/laser_cutter_safety_0.docx | Arts, Engineering
Lead / Other Substance Specific Hazard Awareness | Training | Prior to initial exposure. Refer to OSHA substance-specific standards. | Contact EHS prior to or upon planned use of lead or other OSHA regulated substances. Persons with possible exposure or contact with lead must complete training on the PSU LRN system. | End of calendar year in which course ends or separation of employment + 30 years | LRN Lead / Other Substance Hazard Awareness course | Labs, Engineering, Art studios, Ag, Athletics, M & O Campuses, Police, Student Affairs, OPP, Student Health, Theatre
Lockout/Tagout | LOTO Affected Personnel Training | Initial | Initial training for employees who do not perform LOTO but may be affected by equipment that is LOTO'd | End of calendar year in which course ends or separation of employment + 30 years | EHS - Lockout/Tagout Affected Employee Training | Maintenance, could be anyone
Lockout/Tagout | LOTO contractor notification forms | Prior to contractor beginning work | Work units must exchange LOTO procedures with contractors servicing/maintaining PSU equipment that requires LOTO. This form documents that information exchange. | End of calendar year + 1 year | https://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Lockout/Tagout | LOTO evaluation | Annual - July | Annual evaluation of all employees authorized to use Lockout/Tagout procedures | Period of employment in the work unit | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO lock removal form | As needed | Documentation of lock removal by anyone other than designated employee to whom lock is assigned | End of calendar year + 1 year |  | Maintenance, could be anyone
Lockout/Tagout | LOTO procedures | Initial and update as needed | Documented LOTO procedure is required for equipment with multiple energy sources | Life of equipment | https://ehs.psu.edu/lockout-tagout/forms | Maintenance, could be anyone
Lockout/Tagout | LOTO training | Initial | Initial training for employees who perform Lockout/Tagout | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/lockout-tagout/overview | Maintenance, could be anyone
Machine Shop Safety | Hand & portable power tools pre-use inspection | Prior to each use of equipment | Hand tools and portable power tools must be inspected before each use | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine guarding | Prior to each use of equipment | Ensure that guards are intact and in place prior to each use of equipment. Replace defective or missing guards | N/A | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine Shop Safety training | Initial | General shop safety training is required for all users (employees and students) of shop equipment. Equipment-specific training is required for any equipment with a hazard rating of medium or high. | End of calendar year in which course ends or separation of employment + 30 years | OPP-SAF-Machine Shop Safety Program | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Machine shop self-inspection | Semiannually | Perform semi-annual inspection of machine shops | End of calendar year + 1 year | http://ehs.psu.edu/machine-shop-safety/forms | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Machine Shop Safety | Portable power tools training | Initial | Training is required for personnel who use portable power tools | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/machine-shop-safety/overview | Art Studios, Maintenance, Engineering, Laboratories, Housing & Food Services
Multiple EHS programs | Equipment design standards & approval | Prior to purchase of equipment | Equipment such as autoclaves, laser cutters, fume hoods, biosafety cabinets, eyewash/safety showers, etc. must meet safety design standards. Consult EHS prior to purchase. | Refer to OPP or applicable design standards |  | Any
Multiple EHS programs | Student Activities Review | Prior to event | Student activity requests that involve animals, flame, or any other non-athletic activity that could pose a threat of injury or harm to the environment must be vetted and approved by EHS. | Duration of event | N/A | Student Affairs
Office for Research Protections | Unmanned aircraft (Drones) Plan Review / Request to Fly | Prior to each flight | A "Request to Fly" must be submitted and approved prior to each drone flight. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) registration | Initial | All drones, whether belonging to PSU, individuals, or outside businesses, must be registered with ORP before permission to fly over PSU property will be granted. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Office for Research Protections | Unmanned aircraft (Drones) training | Initial | PSU employees and students wishing to fly drones over PSU property must complete an on-line training. | Maintained by ORP | https://www.research.psu.edu/UasOperations | Any
Personal Protective Equipment | Hazard assessment & PPE determination | Initial, review and update as needed | Supervisor is responsible to document Hazard Assessments regarding PPE use | Until superseded/ updated + 1 year | https://ehs.psu.edu/ppe/forms | All except office
Personal Protective Equipment | Personal Protective Equipment training | Initial | Initial training upon hire, and refresher as needed or when duties change | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment | Personal Protective Equipment training support for supervisors | Initial | A PowerPoint presentation on PPE is available for supervisors to download and customize to their unit's needs | N/A | https://ehs.psu.edu/ppe/resources | All except office
Personal Protective Equipment | PPE inspection | Prior to Use | Visual inspection of PPE prior to each use. Replace as necessary due to wear or age (e.g. hard hats expire at 5 years) | N/A | http://ehs.psu.edu/ppe/overview | All except office
Personal Protective Equipment - Electrical | Electrical glove inspection or replacement | Semiannually | Electrically rated gloves must be inspected by a certified lab or replaced with new gloves every 6 months | N/A | https://ehs.psu.edu/energized-electrical-safety/overview | Maintenance, Engineering | ~$40/pair every 6 months
Radiation | Radon testing | On as needed or case-by-case basis | Consult EHS for questions or concerns regarding radon | End of calendar year in which course ends or separation of employment +30 years |  | OPP, Maintenance
Non-Ionizing Radiation | Accessing rooftops with cell tower installations | As needed | Develop & follow SOP for accessing rooftops that have mobile phone towers installed. This SOP should also be shared with contractors working on the roof. | Keep current version |  | OPP, Maintenance, Housing & Food Services
Radiation Producing Devices | Radiation inspection | Annual | EHS conducts annual inspection of RPDs for leakage, interlock function, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Radiation leakage survey | Varies | Survey after each service, maintenance, or tube change | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices
Radiation Producing Devices | Radiation-producing device Training | Initial | All users of RPDs must complete training prior to operation | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Registration | Initial | Device must be registered within 30 days of arrival at PSU - includes any radiation-producing devices including but not limited to NMR, Electron Microscope, particle accelerators, etc. | Records retained by EHS | http://ehs.psu.edu/radiation-producing-equipment/overview | Labs with x-ray devices (including but not limited to electron microscopes)
Radiation Producing Devices | Repair records | As needed | Retain all repair records | Life of equipment | N/A | Labs with x-ray devices (including but not limited to electron microscopes)
Non-Ionizing Radiation | Hazard Assessment for non-ionizing radiation: microwave, UV, magnetic, IR, RF | Initial | EHS shall review all new installations that emit non-ionizing radiation, including but not limited to cell phone towers, NMR/MRI units, and other radiofrequency-emitting equipment. | Records retained by EHS. Exposure records 30 years plus year generated. | http://ehs.psu.edu/radiation-producing-equipment/overview | Laboratories, OPP
Respirable Crystalline Silica | Exposure control plan | Initial, review and update annually | A written exposure control plan must be created for each work unit with operations including exposure levels exceeding the OSHA Action Level for respirable crystalline silica. This plan must be reviewed annually and updated as necessary. | Superseded/ updated + 1 year | https://ehs.psu.edu/sites/ehs/files/penn_state_written_silica_exposure_control_plan.docx | All except Classroom and Office
Respirable Crystalline Silica | Hazard Assessment | Initial | Each PS work operation with RCS must conduct a screening hazard assessment with any pertinent follow-up exposure monitoring to document as a "negative exposure assessment." | Superseded/ updated + 1 year | https://ehs.psu.edu/Respirable-Crystalline-Silica/Forms | All except Classroom and Office
Respirable Crystalline Silica | Training | Initial | Training is required for all employees who could be exposed to respirable crystalline silica. | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/Respirable-Crystalline-Silica/Requirements-Guidelines | All except Classroom and Office
Respiratory Protection | Hazard Assessment | Initial | Initial hazard assessment to determine applicable exposure and appropriate respiratory protection needs, or voluntary use - Refer to Industrial Hygiene Program | N/A |  | All except Classroom and Office
Respiratory Protection | Medical surveillance | Annual | Annual medical surveillance for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | NA - Records Retained by OCC Med | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator fit testing | Annual | Annual fit test for employees in Respiratory Protection Program. Medical records are retained by Occupational Medicine and/or the third party clinic that performs the testing. | Period of employment in the work unit +1 year | http://ehs.psu.edu/respiratory-protection/overview | All except Classroom and Office
Respiratory Protection | Respirator training (initial) | Initial | Initial on-line/classroom and hands-on respiratory protection training for respirator users | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Respirator training (refresher) | Annual | Annual on-line and hands-on respiratory protection & OSHA requirements review refresher training for employees in Respiratory Protection Program | End of calendar year in which course ends or separation of employment + 30 years | EHS - Respiratory Protection Program | All except Classroom and Office
Respiratory Protection | Voluntary use | As needed | Employees wishing to wear N95 dust masks may do so; the wearing of any tight-fitting (e.g. rubber mask with cartridges) respiratory mask requires annual medical clearance, fit-testing, and training. Voluntary users must also review and sign the prepared Appendix D form ( OSHA 1910.134.), per RPP requirements. | End of calendar year in which use ends or separation of employment + 30 years | https://ehs.psu.edu/sites/ehs/files/penn_state_respiratory_protection_program_apr_2018.docx | All except Classroom and Office
Scaffolds | Scaffold inspection | Daily | Documented inspection by Competent Person required before use. | End of calendar year + 1 year | http://ehs.psu.edu/scaffold-safety/overview | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold inventory | Initial, review and update as needed | Work units must keep an inventory of all scaffolds | Until superseded |  | Maintenance, Athletics, could be anyone
Scaffolds | Scaffold user/erector training | Initial | Training is required for users of scaffold. Additional classroom and hands-on training is required for erectors/disassemblers of scaffold. Re-training is required for newly acquired scaffolding. Fall Protection training may also apply. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Scaffold User Training | Maintenance, Athletics, could be anyone
Spotted Lanternfly Quarantine Implementation | Annual self-audit | Annual - December | Annual self-audit to ensure compliance with the state SLFQ program. | End of calendar year + 1 year | https://ehs.psu.edu/sites/ehs/files/spotted_lanternfly_designated_employee_self-audit.docx | All
Spotted Lanternfly Quarantine Implementation | Designated Employee Training and Unit Permit | Initial | One-time training and permit acquisition through the PA Dep't of Agriculture is required for Spotted Lanternfly Designated employees. | Until superseded | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Driver training | Initial | On-line training for any personnel who will be driving into, out of, or within the SLF quarantine area | End of calendar year in which course ends or separation of employment + 30 years | https://ehs.psu.edu/spotted-lanternfly/overview | All
Spotted Lanternfly Quarantine Implementation | Spotted Lanternfly Training | One-time | All employees who drive in the quarantine zone on University business must take this training. | End of calendar year in which course ends or separation of employment + 30 years |  | All
Spotted Lanternfly Quarantine Implementation | Vehicle Inspection | Prior to moving vehicle | Documented inspection of vehicle when driving within and prior to leaving the SLF quarantine area. | End of calendar year + 2 years | https://ehs.psu.edu/spotted-lanternfly/forms | All
Theater Rigging | Theater Rigging Inspection (annual) | Annual - January | Documented inspection by a Competent Inspector is required annually | Life of equipment | https://ehs.psu.edu/theatre-rigging/forms | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (Third Party) | Every 3 years | Documented inspection by a third party (outside vendor) is required every 3 years. | Life of equipment | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspection (visual) | Prior to Use | Rigging must be visually inspected before each use | N/A | https://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Inspector training | Initial | Training is required for Competent inspectors of theatrical rigging. | End of calendar year in which course ends or separation of employment + 30 years | http://ehs.psu.edu/theatre-rigging/overview | Maintenance, Theater Department faculty/staff
Theater Rigging | Theater Rigging Repair Records | As needed | Retain all repair records | Life of equipment |  | Maintenance, Theater Department faculty/staff
Visual Arts | Visual Arts Safety Plan - Unit Specific Plan | Initial, update annually: August | Prepare a Unit Specific safety plan for each art studio | Superseded/ updated + 1 year | http://ehs.psu.edu/sites/ehs/files/visual_arts_unit_specific_plan_2-14.pdf | Art department faculty, students, staff
Visual Arts | Visual Arts Safety Training (initial) | Initial | Initial Visual Arts Safety training is required for all personnel working in an Art studio | End of calendar year in which course ends or separation of employment + 30 years | EHS - Visual Arts Safety Initial Training - UP | Art department faculty, students, staff
Visual Arts | Visual Arts Safety Training (refresher) | Annual - August | Annual refresher training is required for all personnel working in an Art studio. | End of calendar year in which course ends or separation of employment + 30 years | EHS - Visual Arts Safety Refresher Training - All Locations | Art department faculty, students, staff
Workplace Safety | Post OSHA Job Safety & Health posters | Annual | OSHA's employee information posters are to be posted in a visible place in each occupied building - Most Current Version of Poster to be Displayed | N/A |  | All